## Home
Energy Results Comparison
| Instructions |  | About
| This spreadsheet has been designed to allow the easy comparison of various energy scenarios during early and later design phases using both simulated and postprocessed information. It been optimized to automatically use transcribed data from the scripts, but results from other energy modelling programs or external calculations can be manually inputted. The worksheet can generate graphs and tables for reports and report on LEED points for energy and renewable energy. |  | Energy Results Comparison Worksheet
|  |  | Version: | 4.52
| 1. Enter design and utility information in tab 'Project Information' |  | Last Update: | 2025-11-19
| 2. Perform energy simulations in energy modelling program |  | By: | EJG
| 3. If applicable, use the scripting tools available for each platform to format the results for the universal energy results format |  | Version Notes: | Changed graph and table pages
| 4. If applicable, use the scripting tools to import the Baseline information into the 'BL Data' tab and the Proposed cases into the 'Proposed Data' tab |  |  | Added gross floor area for 2030 reporting table
| 5. Use the 'LEED BL', 'Code BL' and 'Proposed Tabs' to pull in cases from the 'BL Data' and 'Proposed Data' tab |  |  | Updated LEED point calculation
| 6. Use the input cells in these worksheets to postprocess enduse data or to manually add in results from the energy modeling program |  |  | Made provisions for LEED v5
| 7. Use the remaning tabs to generate graphs and tables for reports |  |  | Changed control for including process loads to 'Project Info' page
Refinement to report tables
Fixed bugs in Name
| Legend |  |  | Fixed bugs in renewable energy calculation
Updated the energy cost and carbon factors input methodology
| SI | Cell with pull down menu |  | Added consistency to area for nromalized calculations when conflict between entered value and model
| 2464 | Cell to input information in
| 4928 | Cell that contains a formula and is automatically calculated
Cell does not apply

## Project Info
Project Information
| Project Information |  |  | Worksheet Units
| Project Name |  |  | Select Project Units | IP
| ASHRAE Climate Zone | 4A |  | Select Energy Units for Input | kBtu |  | Specify the units of energy that will be entered in the tables (as output from the energy modelling program)
| Program Type | School |  | Select Energy Units for Output | kBtu |  | Specify the units of energy to report in the tables and graphs. If different from input units, a conversion will be performed
| Gross Conditioned Floor Area | 265425 | ft²
|  |  |  | Additional End Use Categories |  |  | Use this section to define end uses that are not accounted for in the typical end use categories
| Baseline Information |  |  |  | Misc 1 | Misc 2
| AIA 2030 Benchmark EUI (BmEUI) |  | kBtu/ft2 | End Use Name |  |  | Add the names of any atypical end uses that will be used in this project for inclusion in the calcualtions
| AIA 2030 Target Savings | 90% |  | Fuel | Electricity | Gas | Specify fuel type of end use
| LEED Version | LEED v4 |  | Process Load? | No | Yes | Specify if these end uses are a process load or not
| LEED Type | New Construction
| LEED Subcategory | School |  | Site to Source Ratio
| Energy Code Standard | ASHRAE 2010/IECC 2012 |  |  | Electricity | Gas | Additional Fuel | District Cooling | District Heating
| Energy Code Includes Process Loads? | Yes |  | Site to Source Ratio | 2.8 | 1.05 |  | 0.91 | 1.2 | Energy Star US and Canadian Source to Site Ratios
| Performance Goals |  |  | Carbon Emissions Factors
|  | LEED | Code | Select Carbon Emissions Method | Use Calculated Rate |  | Specify if the carbon emissions will be calculated in the flat rates supplied below, or the calculated virtual rate from imported energy model data
Energy Savings Goal
| Carbon Savings Goal |  |  |  | Electricity | Gas | Additional Fuel | District Cooling | District Heating
| Energy Cost Savings Goal |  |  | kg CO2e | 0.465 | 0.05306 |  | 1 | 1 | Energy Star US and Canadian Emissions Factors
|  |  |  | Carbon Units | kWh | kBtu | kWh | kWh | kWh
| QA/QC |  |  | Energy Cost Factors
| Author |  |  | Select Energy Cost Method | Enter Flat Rate |  | Specify if the energy cost will be calculated in the flat rates supplied below, or the calculated virtual rate from imported energy model data
Date
| Uncertainty Factor | 0% |  |  | Electricity | Gas | Additional Fuel | District Cooling | District Heating
|  |  |  | Unit Cost | 0.145 | 1.4 | 2.49 | 1 | 1
|  |  |  | Cost Unit | kWh | Therm | 1000 ft3 Gas | kWh | kWh
Converted Factors
[5 empty] | Electricity | Gas | Additional Fuel | District Cooling | District Heating
|  |  |  | Carbon Flat Rate Converted | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | Flat Rate Unit Price Converted | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
|  |  |  | LEED Baseline | 0 | 0 | 0 | 0 | 0
|  |  |  | Compliance Baseline | 0 | 0 | 0 | 0 | 0
|  |  |  | Proposed Design | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | LEED Baseline | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | Compliance Baseline | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | Proposed Case 1 | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | Proposed Case 2 | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | Proposed Case 3 | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | Proposed Case 4 | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | Proposed Case 5 | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | Proposed Case 6 | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | Proposed Case 7 | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | Proposed Case 8 | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | Proposed Case 9 | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | Proposed Case 10 | 0.13628 | 0.05306 | 0 | 0.29307 | 0.29307
|  |  |  | LEED Baseline | 0.042497 | 0 | 0 | 0 | 0
|  |  |  | Compliance Baseline | 0.042497 | 0 | 0 | 0 | 0
|  |  |  | Proposed Design | 0.042497 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | LEED Baseline | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
|  |  |  | Compliance Baseline | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
|  |  |  | Proposed Case 1 | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
|  |  |  | Proposed Case 2 | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
|  |  |  | Proposed Case 3 | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
|  |  |  | Proposed Case 4 | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
|  |  |  | Proposed Case 5 | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
|  |  |  | Proposed Case 6 | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
|  |  |  | Proposed Case 7 | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
|  |  |  | Proposed Case 8 | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
|  |  |  | Proposed Case 9 | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
|  |  |  | Proposed Case 10 | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307
Note on D7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use this field to enter a custom area, otherwise the area will be automatically taken from the simulations scraped to the 'Proposed Data' tab.

## BL Data
Option | Results Path | Timestamp | Climate File | Climate Zone | Heating Unmet Hours | Cooling Unmet Hours | Total Energy Use (kBtu) | Energy Use Intensity (kBtu/ft²) | Electricity (kBtu) | Gas (kBtu) | Additional Fuel (kBtu) | District Cooling (kBtu) | District Heating (kBtu) | Heating - Electricity Energy Use (kBtu) | Heating - Gas Energy Use (kBtu) | Heating - Additonal Fuel Energy Use (kBtu) | Heating - District Heating Energy Use (kBtu) | Cooling - Electricity Energy Use (kBtu) | Cooling - District Energy Use (kBtu) | Interior Lighting - Electricity Energy Use (kBtu) | Exterior Lighting - Electricity Energy Use (kBtu) | Interior Equipment - Electricity Energy Use (kBtu) | Interior Equipment - Gas Energy Use (kBtu) | Interior Equipment - Additional Fuel Energy Use (kBtu) | Exterior Equipment - Energy Use (kBtu) | Fans - Electricity Energy Use (kBtu) | Pumps - Electricity Energy Use (kBtu) | Heat Rejection - Electricity Energy Use (kBtu) | Humidification - Electricity Energy Use (kBtu) | Heat Recovery - Electricity Energy Use (kBtu) | Water Systems - Electricity Energy Use (kBtu) | Water Systems - Gas Energy Use (kBtu) | Water Systems - Additional Fuel Energy Use (kBtu) | Water Systems - District Heating Energy Use (kBtu) | Refrigeration - Electricity Energy Use (kBtu) | Generators Electricity Energy Use (kBtu) | Misc 1 - Electricity Energy Use (kBtu) | Misc 2 - Electricity Energy Use (kBtu) | Total Water Use (kGal) | Water Use Intensity (kGal/ft²) | Heat Rejection - Water Use (kGal) | Humidificatopn - Water Use (kGal) | Water System - Water Use (kGal) | Total Energy Cost ($) | Energy Cost Intensity ($/ft²) | Electricity Virtual Rate ($/kBtu) | Gas Virtual Rate ($/kBtu) | Additional Fuel Virtual Rate ($/kBtu) | District Cooling Virtual Rate ($/kBtu) | District Heating Virtual Rate ($/kBtu) | Total Carbon Emissions (kg CO2e) | Carbon Emission Intensity (kg CO2e/ft²) | Electricity Virtual Rate (kg CO2e/kBtu) | Gas Virtual Rate (kg CO2e/kBtu) | Additional Fuel Virtual Rate (kg CO2e/kBtu) | District Cooling Virtual Rate (kg CO2e/kBtu) | District Heating Virtual Rate (kg CO2e/kBtu) | Peak Heating (kBtuh) | Peak Heating (Btuh/ft²) | Peak Heating Hour | Peak Cooling (kBtuh) | Peak Cooling (Btuh/ft²) | Peak Cooling Hour | Peak Electrical Load (W) | Peak Electrical Load Intensity (W/ft²) | Peak Electricity Hour | Conditioned Floor Area (ft²) | Total Floor Area (ft²) | Gross Wall Area (ft²) | Above Ground Gross Wall Area (ft²) | Above Ground North Wall Area (ft²) | Above Ground East Wall Area (ft²) | Above Ground South Wall Area (ft²) | Above Ground East Wall Area (ft²) | North WWR Nominal (%) | East WWR Nominal (%) | South WWR Nominal (%) | West WWR Nominal (%) | Building WWR Actual (%) | North WWR Actual (%) | East WWR Actual (%) | South WWR Actual (%) | West WWR Actual (%) | Gross Roof Area (ft²) | Skylight Roof Ratio (%) | Exterior Wall to Floor Area Ratio | Exterior Roof to Floor Area Ratio | Exterior Envelope to Floor Area Ratio | North Shading Type | North Shading Ratio (%) | West Shading Type | West Shading Ratio (%) | South Shading Type | South Shading Ratio (%) | East Shading Type | East Shading Ratio (%) | Vertical Weighted U-Value (Btu/h·ft²·F) | Vertical Weighted R-Value (ft²·h·F/Btu ) | Wall U-Value (Btu/h·ft²·F) | Wall 2 U-Value (Btu/h·ft²·F) | Roof U-Value (Btu/h·ft²·F) | Exposed Floor U-Value (Btu/h·ft²·F) | Slab on Grade U-Value (Btu/h·ft²·F) | Assembly U-Value (Btu/h·ft²·F) | Glass U-Value (Btu/h·ft²·F) | Glass SHGC | Glass VLT | Glass LSG | Infiltration Rate (CFM/ft² facade) | Lighting Power Density (W/ft²) | Conditioned Lighting Power Density (W/ft²) | Occupant Density (ft²/person) | Conditioned Occupant Density (ft²/person) | Equipment Power Density (W/ft²) | Conditioned Equipment Power Density (W/ft²) | Total Ventilation Air Flow Rate (CFM) | Ventilation Air Flow Rate per Area (CFM/ft²) | Total Heating Airflow Rate (CFM) | Heating Airflow Rate per Area (CFM/ft²) | Total Cooling Airflow Rate (CFM) | Cooling Airflow Rate per Area (CFM/ft²) | Chiller Efficiency (COP) | Boiler Efficiency (COP) | DX Cooling Efficiency (COP) | DX Heating Efficiency (HSPF) | Heat Pump Cooling Efficiency (COP) | Heat Pump Heating Efficiency (COP) | Total Fan Power (kW) | Total Pump Power (kW) | Service Hot Water Thermal Efficiency (COP) | Exterior Lighting (kW)
LEED Baseline | MSU Energy Model_LEED_0 - Baseline Design.SIM | 5/06/2026 21:42:44 | Baltimore MD TMY2 | 4A | 1342 | 648 | 32420600 | 122.1 | 32421000 | 0 |  |  |  | 11180000 | 0 |  |  | 4119000 |  | 2580000 | 0 | 7093000 | 0 |  |  | 2987000 | 3803000 | 275200 |  |  | 387700 | 0 |  |  | 0 | [8 empty] | 1377388 | 5.19 | 0.042497 | 0 | [10 empty] | 6004.215 | 22.6211 | JAN 15 08:00 | 10824.753 | 40.7827 | JUL 24 13:00 | 4689846 | 17.6692 | 3 | 265425 | 265425 | 92288.58 | 92288.58 | 7945.14 | 8754.56 | 2730.95 | 1050.01 |  |  |  |  | 34.8339 | 38.337 | 37.0477 | 51.9874 | 37.7311 | 274038.78 | 0.79589 | 0.3477 | 1.0325 | 1.3802 | [8 empty] | 0.192 | 5.2083 | 0.062 |  | 0.047 |  | 0.027 | 0.079 | 0.435 | 0.878 | 0.9 | 1.0251 | 0.039158 | 1.1876 | 1.1908 | 92.5148 | 92.2633 | 2.4803 | 2.4871 | 253316 | 0.95438 | 253316 | 0.95438 | 253316 | 0.95438 | 5 | 0.97992 |  |  |  |  | 329.33 | 228.131 | 1
LEED Baseline 90° | MSU Energy Model_LEED_90 - Baseline Design.SIM | 5/06/2026 22:41:19 | Baltimore MD TMY2 | 4A | 2220 | 709 | 32022500 | 120.6 | 32022000 | 0 |  |  |  | 9115000 | 0 |  |  | 4464000 |  | 2580000 | 0 | 7093000 | 0 |  |  | 4153000 | 3939000 | 290700 |  |  | 387700 | 0 |  |  | 0 | [8 empty] | 1360474 | 5.13 | 0.042497 | 0 | [10 empty] | 3786.429 | 14.2655 | JAN 15 08:00 | 10987.026 | 41.3941 | JUL 24 13:00 | 4827222 | 18.1868 | 9 | 265425 | 265425 | 92288.63 | 92288.63 | 14581.71 | 4598.75 | 8754.56 | 2730.95 |  |  |  |  | 34.8338 | 31.9644 | 38.0066 | 37.0477 | 51.9874 | 274038.78 | 0.79589 | 0.3477 | 1.0325 | 1.3802 | [8 empty] | 0.192 | 5.2083 | 0.062 |  | 0.047 |  | 0.027 | 0.079 | 0.435 | 0.878 | 0.9 | 1.0251 | 0.039158 | 1.1876 | 1.1908 | 92.5148 | 92.2633 | 2.4803 | 2.4871 | 250322 | 0.9431 | 250322 | 0.9431 | 250322 | 0.9431 | 5 | 0.97992 |  |  |  |  | 455.341 | 234.066 | 1
LEED Baseline 180° | MSU Energy Model_LEED_180 - Baseline Design.SIM | 5/06/2026 22:49:58 | Baltimore MD TMY2 | 4A | 2178 | 743 | 32152800 | 121.1 | 32153000 | 0 |  |  |  | 9174000 | 0 |  |  | 4491000 |  | 2580000 | 0 | 7093000 | 0 |  |  | 4184000 | 3950000 | 292800 |  |  | 387700 | 0 |  |  | 0 | [8 empty] | 1366011 | 5.15 | 0.042497 | 0 | [10 empty] | 3815.047 | 14.3734 | JAN 15 08:00 | 11146.494 | 41.9949 | JUL 24 13:00 | 4325164 | 16.2952 | 2/26 | 265425 | 265425 | 92288.71 | 92288.71 | 3880.08 | 1050.01 | 4598.75 | 8754.56 |  |  |  |  | 34.8338 | 43.6669 | 37.7311 | 38.0066 | 37.0477 | 274038.78 | 0.79589 | 0.3477 | 1.0325 | 1.3802 | [8 empty] | 0.192 | 5.2083 | 0.062 |  | 0.047 |  | 0.027 | 0.079 | 0.435 | 0.878 | 0.9 | 1.0251 | 0.039158 | 1.1876 | 1.1908 | 92.5148 | 92.2633 | 2.4803 | 2.4871 | 252037 | 0.94956 | 252037 | 0.94956 | 252037 | 0.94956 | 5 | 0.97992 |  |  |  |  | 457.761 | 234.757 | 1
LEED Baseline 270° | MSU Energy Model_LEED_270 - Baseline Design.SIM | 5/06/2026 22:55:46 | Baltimore MD TMY2 | 4A | 2243 | 683 | 32104300 | 121 | 32104000 | 0 |  |  |  | 9165000 | 0 |  |  | 4472000 |  | 2580000 | 0 | 7093000 | 0 |  |  | 4173000 | 3942000 | 291000 |  |  | 387700 | 0 |  |  | 0 | [8 empty] | 1363952 | 5.14 | 0.042497 | 0 | [10 empty] | 3805.309 | 14.3367 | JAN 15 08:00 | 11004.142 | 41.4586 | JUL 24 13:00 | 4600541 | 17.3327 | 9 | 265425 | 265425 | 92288.66 | 92288.66 | 19140.12 | 2730.95 | 1050.01 | 4598.75 |  |  |  |  | 34.8338 | 33.8004 | 51.9874 | 37.7311 | 38.0066 | 274038.78 | 0.79589 | 0.3477 | 1.0325 | 1.3802 | [8 empty] | 0.192 | 5.2083 | 0.062 |  | 0.047 |  | 0.027 | 0.079 | 0.435 | 0.878 | 0.9 | 1.0251 | 0.039158 | 1.1876 | 1.1908 | 92.5148 | 92.2633 | 2.4803 | 2.4871 | 250419 | 0.94346 | 250419 | 0.94346 | 250419 | 0.94346 | 5 | 0.97992 |  |  |  |  | 455.808 | 234.139 | 1
Compliance Baseline | MSU Energy Model_Compliance_0 - Baseline Design.SIM | 5/06/2026 14:56:30 | Baltimore MD TMY2 | 4A | 1339 | 512 | 38537700 | 145.2 | 38538000 | 0 |  |  |  | 10470000 | 0 |  |  | 5864000 |  | 2487000 | 0 | 7093000 | 0 |  |  | 7695000 | 4204000 | 335200 |  |  | 387700 | 0 |  |  | 0 | [8 empty] | 1637275 | 6.17 | 0.042497 | 0 | [10 empty] | 5948.294 | 22.4105 | JAN 15 08:00 | 13320.469 | 50.1854 | JUL 24 10:00 | 4906833 | 18.4867 | 10/19 | 265425 | 265425 | 92288.58 | 92288.58 | 7945.14 | 8754.56 | 2730.95 | 1050.01 |  |  |  |  | 34.8339 | 38.337 | 37.0477 | 51.9874 | 37.7311 | 274038.78 | 0.79589 | 0.3477 | 1.0325 | 1.3802 | [8 empty] | 0.267 | 3.7453 | 0.118 |  | 0.061 |  | 0.027 | 0.105 | 0.487 | 0.878 | 0.9 | 1.0251 | 0.039158 | 1.1446 | 1.1578 | 92.5148 | 91.4634 | 2.4803 | 2.5088 | 256283 | 0.96556 | 256283 | 0.96556 | 256283 | 0.96556 | 4.4053 | 0.97992 |  |  |  |  | 919.249 | 247.535 | 1
Compliance 90° | MSU Energy Model_Compliance_90 - Baseline Design.SIM | 5/06/2026 13:25:42 | Baltimore MD TMY2 | 4A | 1373 | 576 | 38144500 | 143.7 | 38144000 | 0 |  |  |  | 10350000 | 0 |  |  | 5776000 |  | 2487000 | 0 | 7093000 | 0 |  |  | 7549000 | 4170000 | 330000 |  |  | 387700 | 0 |  |  | 0 | [8 empty] | 1620569 | 6.11 | 0.042497 | 0 | [10 empty] | 5844.589 | 22.0197 | JAN 15 08:00 | 12902.2 | 48.6096 | JUL 24 10:00 | 4905025 | 18.4799 | 7/15 | 265425 | 265425 | 92288.63 | 92288.63 | 14581.71 | 4598.75 | 8754.56 | 2730.95 |  |  |  |  | 34.8338 | 31.9644 | 38.0066 | 37.0477 | 51.9874 | 274038.78 | 0.79589 | 0.3477 | 1.0325 | 1.3802 | [8 empty] | 0.267 | 3.7453 | 0.118 |  | 0.061 |  | 0.027 | 0.105 | 0.487 | 0.878 | 0.9 | 1.0251 | 0.039158 | 1.1446 | 1.1578 | 92.5148 | 91.4634 | 2.4803 | 2.5088 | 252492 | 0.95127 | 252492 | 0.95127 | 252492 | 0.95127 | 4.4053 | 0.97992 |  |  |  |  | 905.917 | 245.693 | 1
Compliance 180° | MSU Energy Model_Compliance_180 - Baseline Design.SIM | 5/06/2026 13:30:28 | Baltimore MD TMY2 | 4A | 1317 | 589 | 38361100 | 144.5 | 38361000 | 0 |  |  |  | 10450000 | 0 |  |  | 5817000 |  | 2487000 | 0 | 7093000 | 0 |  |  | 7611000 | 4186000 | 332800 |  |  | 387700 | 0 |  |  | 0 | [8 empty] | 1629770 | 6.14 | 0.042497 | 0 | [10 empty] | 5929.956 | 22.3414 | JAN 15 08:00 | 13278.192 | 50.0262 | JUL 24 10:00 | 4757815 | 17.9253 | 5 | 265425 | 265425 | 92288.71 | 92288.71 | 3880.08 | 1050.01 | 4598.75 | 8754.56 |  |  |  |  | 34.8338 | 43.6669 | 37.7311 | 38.0066 | 37.0477 | 274038.78 | 0.79589 | 0.3477 | 1.0325 | 1.3802 | [8 empty] | 0.267 | 3.7453 | 0.118 |  | 0.061 |  | 0.027 | 0.105 | 0.487 | 0.878 | 0.9 | 1.0251 | 0.039158 | 1.1446 | 1.1578 | 92.5148 | 91.4634 | 2.4803 | 2.5088 | 254822 | 0.96005 | 254822 | 0.96005 | 254822 | 0.96005 | 4.4053 | 0.97992 |  |  |  |  | 912.296 | 246.713 | 1
Compliance 270° | MSU Energy Model_Compliance_270 - Baseline Design.SIM | 5/06/2026 13:34:11 | Baltimore MD TMY2 | 4A | 1304 | 561 | 38271800 | 144.2 | 38272000 | 0 |  |  |  | 10420000 | 0 |  |  | 5791000 |  | 2487000 | 0 | 7093000 | 0 |  |  | 7591000 | 4174000 | 330700 |  |  | 387700 | 0 |  |  | 0 | [8 empty] | 1625978 | 6.13 | 0.042497 | 0 | [10 empty] | 5857.743 | 22.0693 | JAN 15 08:00 | 12950.179 | 48.7904 | JUL 24 10:00 | 4911153 | 18.503 | 7/15 | 265425 | 265425 | 92288.66 | 92288.66 | 19140.12 | 2730.95 | 1050.01 | 4598.75 |  |  |  |  | 34.8338 | 33.8004 | 51.9874 | 37.7311 | 38.0066 | 274038.78 | 0.79589 | 0.3477 | 1.0325 | 1.3802 | [8 empty] | 0.267 | 3.7453 | 0.118 |  | 0.061 |  | 0.027 | 0.105 | 0.487 | 0.878 | 0.9 | 1.0251 | 0.039158 | 1.1446 | 1.1578 | 92.5148 | 91.4634 | 2.4803 | 2.5088 | 252774 | 0.95234 | 252774 | 0.95234 | 252774 | 0.95234 | 4.4053 | 0.97992 |  |  |  |  | 907.65 | 245.853 | 1

## Proposed Data
Option | Results Path | Timestamp | Climate File | Climate Zone | Heating Unmet Hours | Cooling Unmet Hours | Total Energy Use (kBtu) | Energy Use Intensity (kBtu/ft²) | Electricity (kBtu) | Gas (kBtu) | Additional Fuel (kBtu) | District Cooling (kBtu) | District Heating (kBtu) | Heating - Electricity Energy Use (kBtu) | Heating - Gas Energy Use (kBtu) | Heating - Additonal Fuel Energy Use (kBtu) | Heating - District Heating Energy Use (kBtu) | Cooling - Electricity Energy Use (kBtu) | Cooling - District Energy Use (kBtu) | Interior Lighting - Electricity Energy Use (kBtu) | Exterior Lighting - Electricity Energy Use (kBtu) | Interior Equipment - Electricity Energy Use (kBtu) | Interior Equipment - Gas Energy Use (kBtu) | Interior Equipment - Additional Fuel Energy Use (kBtu) | Exterior Equipment - Energy Use (kBtu) | Fans - Electricity Energy Use (kBtu) | Pumps - Electricity Energy Use (kBtu) | Heat Rejection - Electricity Energy Use (kBtu) | Humidification - Electricity Energy Use (kBtu) | Heat Recovery - Electricity Energy Use (kBtu) | Water Systems - Electricity Energy Use (kBtu) | Water Systems - Gas Energy Use (kBtu) | Water Systems - Additional Fuel Energy Use (kBtu) | Water Systems - District Heating Energy Use (kBtu) | Refrigeration - Electricity Energy Use (kBtu) | Generators Electricity Energy Use (kBtu) | Misc 1 - Electricity Energy Use (kBtu) | Misc 2 - Electricity Energy Use (kBtu) | Total Water Use (kGal) | Water Use Intensity (kGal/ft²) | Heat Rejection - Water Use (kGal) | Humidificatopn - Water Use (kGal) | Water System - Water Use (kGal) | Total Energy Cost ($) | Energy Cost Intensity ($/ft²) | Electricity Virtual Rate ($/kBtu) | Gas Virtual Rate ($/kBtu) | Additional Fuel Virtual Rate ($/kBtu) | District Cooling Virtual Rate ($/kBtu) | District Heating Virtual Rate ($/kBtu) | Total Carbon Emissions (kg CO2e) | Carbon Emission Intensity (kg CO2e/ft²) | Electricity Virtual Rate (kg CO2e/kBtu) | Gas Virtual Rate (kg CO2e/kBtu) | Additional Fuel Virtual Rate (kg CO2e/kBtu) | District Cooling Virtual Rate (kg CO2e/kBtu) | District Heating Virtual Rate (kg CO2e/kBtu) | Peak Heating (kBtuh) | Peak Heating (Btuh/ft²) | Peak Heating Hour | Peak Cooling (kBtuh) | Peak Cooling (Btuh/ft²) | Peak Cooling Hour | Peak Electrical Load (W) | Peak Electrical Load Intensity (W/ft²) | Peak Electricity Hour | Conditioned Floor Area (ft²) | Total Floor Area (ft²) | Gross Wall Area (ft²) | Above Ground Gross Wall Area (ft²) | Above Ground North Wall Area (ft²) | Above Ground East Wall Area (ft²) | Above Ground South Wall Area (ft²) | Above Ground East Wall Area (ft²) | North WWR Nominal (%) | East WWR Nominal (%) | South WWR Nominal (%) | West WWR Nominal (%) | Building WWR Actual (%) | North WWR Actual (%) | East WWR Actual (%) | South WWR Actual (%) | West WWR Actual (%) | Gross Roof Area (ft²) | Skylight Roof Ratio (%) | Exterior Wall to Floor Area Ratio | Exterior Roof to Floor Area Ratio | Exterior Envelope to Floor Area Ratio | North Shading Type | North Shading Ratio (%) | West Shading Type | West Shading Ratio (%) | South Shading Type | South Shading Ratio (%) | East Shading Type | East Shading Ratio (%) | Vertical Weighted U-Value (Btu/h·ft²·F) | Vertical Weighted R-Value (ft²·h·F/Btu ) | Wall U-Value (Btu/h·ft²·F) | Wall 2 U-Value (Btu/h·ft²·F) | Roof U-Value (Btu/h·ft²·F) | Exposed Floor U-Value (Btu/h·ft²·F) | Slab on Grade U-Value (Btu/h·ft²·F) | Assembly U-Value (Btu/h·ft²·F) | Glass U-Value (Btu/h·ft²·F) | Glass SHGC | Glass VLT | Glass LSG | Infiltration Rate (CFM/ft² facade) | Lighting Power Density (W/ft²) | Conditioned Lighting Power Density (W/ft²) | Occupant Density (ft²/person) | Conditioned Occupant Density (ft²/person) | Equipment Power Density (W/ft²) | Conditioned Equipment Power Density (W/ft²) | Total Ventilation Air Flow Rate (CFM) | Ventilation Air Flow Rate per Area (CFM/ft²) | Total Heating Airflow Rate (CFM) | Heating Airflow Rate per Area (CFM/ft²) | Total Cooling Airflow Rate (CFM) | Cooling Airflow Rate per Area (CFM/ft²) | Chiller Efficiency (COP) | Boiler Efficiency (COP) | DX Cooling Efficiency (COP) | DX Heating Efficiency (HSPF) | Heat Pump Cooling Efficiency (COP) | Heat Pump Heating Efficiency (COP) | Total Fan Power (kW) | Total Pump Power (kW) | Service Hot Water Thermal Efficiency (COP) | Exterior Lighting (kW)
Proposed Design | MSU Energy Model_Proposed - Baseline Design.SIM | 5/06/2026 21:15:46 | Baltimore MD TMY2 | 4A | 1076 | 659 | 25583100 | 96.1 | 25583000 | 0 |  |  |  | 1397000 | 0 |  |  | 3678000 |  | 1758000 | 0 | 7104000 | 0 |  |  | 10080000 | 1066000 | 0 |  |  | 495500 | 0 |  |  | 0 | [8 empty] | 1086897 | 4.08 | 0.042497 | 0 | [10 empty] | 4816.227 | 18.0963 | JAN 20 08:00 | 12468.677 | 46.8494 | JUL 24 10:00 | 3048247 | 11.4534 | 7/24 | 265425 | 265425 | 92069.74 | 92069.74 | 7945.14 | 8754.56 | 2730.95 | 1050.01 |  |  |  |  | 34.5323 | 36.1931 | 37.0477 | 51.9874 | 37.7311 | 274024.41 | 0.79593 | 0.34594 | 1.0296 | 1.3755 | [8 empty] | 0.236 | 4.2373 | 0.054 |  | 0.042 |  | 0.027 | 0.086 | 0.52625 | 0.40783 | 0.51715 | 1.2681 | 0.03906 | 0.8073 | 0.82043 | 92.8625 | 91.3762 | 2.4728 | 2.513 | 344150 | 1.2931 | 344150 | 1.2931 | 344150 | 1.2931 | 2.7953 | 0.97743 |  |  |  |  | 1090.289 | 504.648 | 1

## LEED BL
LEED Baseline Results Worksheet
Instructions
If the 'BL Data' tab has been populated with the LEED and Code baseline rotations by a script, use the pulldowns next to the 'Baseline Case' to choose if only the 0 degree rotation or the average of all rotations should be used. The results will automatically be pulled in from the database. Use the input cells to manually input values without using the database, or to override or add to database values.
LEED Baseline Results Worksheet 0° Rotation
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand | [6 empty] | Energy Results
| Baseline Case | Average of All Baselines |  |  | Imported Data | LEED Baseline |  | MSU Energy Model_LEED_0 - Baseline Design.SIM | [5 empty] | 5/06/2026 21:42:44 |  |  | 4689.846 | kW | [5 empty] | Total | 32424900 | kBtu
| Area | 265425 | ft² |  | Manual Input | [12 empty] | kW | [6 empty] | 122.1622 | kBtu/ft²
[5 empty] | Value Used | LEED Baseline |  | MSU Energy Model_LEED_0 - Baseline Design.SIM | [5 empty] | 5/06/2026 21:42:44 |  |  | 4689.846 | kW
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 11180000 | 0 | 0 | 0 | 4119000 | 0 | 2580000 | 0 | 7093000 | 0 | 0 | 0 | 2987000 | 3803000 | 275200 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 11180000 | 0 | 0 | 0 | 4119000 | 0 | 2580000 | 0 | 7093000 | 0 | 0 | 0 | 2987000 | 3803000 | 275200 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEED Baseline Results Worksheet 90° Rotation
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand | [6 empty] | Energy Results
[5 empty] | Imported Data | LEED Baseline 90° |  | MSU Energy Model_LEED_90 - Baseline Design.SIM | [5 empty] | 5/06/2026 22:41:19 |  |  | 4827.222 | kW | [5 empty] | Total | 32022400 | kBtu
[5 empty] | Manual Input | [12 empty] | kW | [6 empty] | 120.6458 | kBtu/ft²
[5 empty] | Value Used | LEED Baseline 90° |  | MSU Energy Model_LEED_90 - Baseline Design.SIM | [5 empty] | 5/06/2026 22:41:19 |  |  | 4827.222 | kW
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 9115000 | 0 | 0 | 0 | 4464000 | 0 | 2580000 | 0 | 7093000 | 0 | 0 | 0 | 4153000 | 3939000 | 290700 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 9115000 | 0 | 0 | 0 | 4464000 | 0 | 2580000 | 0 | 7093000 | 0 | 0 | 0 | 4153000 | 3939000 | 290700 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEED Baseline Results Worksheet 180° Rotation
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand | [6 empty] | Energy Results
[5 empty] | Imported Data | LEED Baseline 180° |  | MSU Energy Model_LEED_180 - Baseline Design.SIM | [5 empty] | 5/06/2026 22:49:58 |  |  | 4325.164 | kW | [5 empty] | Total | 32152500 | kBtu
[5 empty] | Manual Input | [12 empty] | kW | [6 empty] | 121.1359 | kBtu/ft²
[5 empty] | Value Used | LEED Baseline 180° |  | MSU Energy Model_LEED_180 - Baseline Design.SIM | [5 empty] | 5/06/2026 22:49:58 |  |  | 4325.164 | kW
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 9174000 | 0 | 0 | 0 | 4491000 | 0 | 2580000 | 0 | 7093000 | 0 | 0 | 0 | 4184000 | 3950000 | 292800 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 9174000 | 0 | 0 | 0 | 4491000 | 0 | 2580000 | 0 | 7093000 | 0 | 0 | 0 | 4184000 | 3950000 | 292800 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEED Baseline Results Worksheet 270° Rotation
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand | [6 empty] | Energy Results
[5 empty] | Imported Data | LEED Baseline 270° |  | MSU Energy Model_LEED_270 - Baseline Design.SIM | [5 empty] | 5/06/2026 22:55:46 |  |  | 4600.541 | kW | [5 empty] | Total | 32103700 | kBtu
[5 empty] | Manual Input | [12 empty] | kW | [6 empty] | 120.9521 | kBtu/ft²
[5 empty] | Value Used | LEED Baseline 270° |  | MSU Energy Model_LEED_270 - Baseline Design.SIM | [5 empty] | 5/06/2026 22:55:46 |  |  | 4600.541 | kW
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 9165000 | 0 | 0 | 0 | 4472000 | 0 | 2580000 | 0 | 7093000 | 0 | 0 | 0 | 4173000 | 3942000 | 291000 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 9165000 | 0 | 0 | 0 | 4472000 | 0 | 2580000 | 0 | 7093000 | 0 | 0 | 0 | 4173000 | 3942000 | 291000 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Code BL
Code Baseline Results Worksheet
Instructions
If the 'BL Data' tab has been populated with the LEED and Code baseline rotations by a script, use the pulldowns next to the 'Baseline Case' to choose if only the 0 degree rotation or the average of all rotations should be used. The results will automatically be pulled in from the database. Use the input cells to manually input values without using the database, or to override or add to database values.
Code Baseline Results Worksheet 0° Rotation
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand | [6 empty] | Energy Results
| Baseline Case | Average of All Baselines |  |  | Imported Data | Compliance Baseline |  | MSU Energy Model_Compliance_0 - Baseline Design.SIM | [5 empty] | 5/06/2026 14:56:30 |  |  | 4906.833 | kW | [5 empty] | Total | 38535900 | kBtu
| Area | 265425 | ft² |  | Manual Input | [12 empty] | kW | [6 empty] | 145.1856 | kBtu/ft²
[5 empty] | Value Used | Compliance Baseline |  | MSU Energy Model_Compliance_0 - Baseline Design.SIM | [5 empty] | 5/06/2026 14:56:30 |  |  | 4906.833 | kW
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 10470000 | 0 | 0 | 0 | 5864000 | 0 | 2487000 | 0 | 7093000 | 0 | 0 | 0 | 7695000 | 4204000 | 335200 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 10470000 | 0 | 0 | 0 | 5864000 | 0 | 2487000 | 0 | 7093000 | 0 | 0 | 0 | 7695000 | 4204000 | 335200 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Code Baseline Results Worksheet 90° Rotation
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand | [6 empty] | Energy Results
[5 empty] | Imported Data | Compliance 90° |  | MSU Energy Model_Compliance_90 - Baseline Design.SIM | [5 empty] | 5/06/2026 13:25:42 |  |  | 4905.025 | kW | [5 empty] | Total | 38142700 | kBtu
[5 empty] | Manual Input | [12 empty] | kW | [6 empty] | 143.7042 | kBtu/ft²
[5 empty] | Value Used | Compliance 90° |  | MSU Energy Model_Compliance_90 - Baseline Design.SIM | [5 empty] | 5/06/2026 13:25:42 |  |  | 4905.025 | kW
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 10350000 | 0 | 0 | 0 | 5776000 | 0 | 2487000 | 0 | 7093000 | 0 | 0 | 0 | 7549000 | 4170000 | 330000 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 10350000 | 0 | 0 | 0 | 5776000 | 0 | 2487000 | 0 | 7093000 | 0 | 0 | 0 | 7549000 | 4170000 | 330000 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Code Baseline Results Worksheet 180° Rotation
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand | [6 empty] | Energy Results
[5 empty] | Imported Data | Compliance 180° |  | MSU Energy Model_Compliance_180 - Baseline Design.SIM | [5 empty] | 5/06/2026 13:30:28 |  |  | 4757.815 | kW | [5 empty] | Total | 38364500 | kBtu
[5 empty] | Manual Input | [12 empty] | kW | [6 empty] | 144.5399 | kBtu/ft²
[5 empty] | Value Used | Compliance 180° |  | MSU Energy Model_Compliance_180 - Baseline Design.SIM | [5 empty] | 5/06/2026 13:30:28 |  |  | 4757.815 | kW
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 10450000 | 0 | 0 | 0 | 5817000 | 0 | 2487000 | 0 | 7093000 | 0 | 0 | 0 | 7611000 | 4186000 | 332800 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 10450000 | 0 | 0 | 0 | 5817000 | 0 | 2487000 | 0 | 7093000 | 0 | 0 | 0 | 7611000 | 4186000 | 332800 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Code Baseline Results Worksheet 270° Rotation
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand | [6 empty] | Energy Results
[5 empty] | Imported Data | Compliance 270° |  | MSU Energy Model_Compliance_270 - Baseline Design.SIM | [5 empty] | 5/06/2026 13:34:11 |  |  | 4911.153 | kW | [5 empty] | Total | 38274400 | kBtu
[5 empty] | Manual Input | [12 empty] | kW | [6 empty] | 144.2004 | kBtu/ft²
[5 empty] | Value Used | Compliance 270° |  | MSU Energy Model_Compliance_270 - Baseline Design.SIM | [5 empty] | 5/06/2026 13:34:11 |  |  | 4911.153 | kW
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 10420000 | 0 | 0 | 0 | 5791000 | 0 | 2487000 | 0 | 7093000 | 0 | 0 | 0 | 7591000 | 4174000 | 330700 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 10420000 | 0 | 0 | 0 | 5791000 | 0 | 2487000 | 0 | 7093000 | 0 | 0 | 0 | 7591000 | 4174000 | 330700 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Proposed
Proposed Case(s) Results Worksheet
Instructions
If the 'Proposed Data' tab has been populated with alternatives with a script, use the pulldowns next to the 'Select Case' to choose the parametric scenario to use as the proposed case. The results will automatically be pulled in from the database. Use the input cells to manually input values without using the database, or to override or add to database values.
Proposed Case 1
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand |  |  | Renewable Energy Generation |  |  |  | Energy Results
| Select Case | Proposed Design |  |  | Imported Data | Proposed Design |  | MSU Energy Model_Proposed - Baseline Design.SIM | [5 empty] | 5/06/2026 21:15:46 |  |  | 3048.247 | kW |  | PV | Wind | SolarHW |  | Total | 25578500 | kBtu
| Area | 265425 | ft² |  | Manual Input | [12 empty] | kW | [6 empty] | 96.3681 | kBtu/ft²
[5 empty] | Value Used | Proposed Design |  | MSU Energy Model_Proposed - Baseline Design.SIM | [5 empty] | 5/06/2026 21:15:46 |  |  | 3048.247 | kW |  | kWh | kWh | kWh
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 1397000 | 0 | 0 | 0 | 3678000 | 0 | 1758000 | 0 | 7104000 | 0 | 0 | 0 | 10080000 | 1066000 | 0 | 0 | 0 | 495500 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 1397000 | 0 | 0 | 0 | 3678000 | 0 | 1758000 | 0 | 7104000 | 0 | 0 | 0 | 10080000 | 1066000 | 0 | 0 | 0 | 495500 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed Case 2
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand |  |  | Renewable Energy Generation |  |  |  | Energy Results
| Select Case |  |  |  | Imported Data | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | PV | Wind | SolarHW |  | Total | 0 | kBtu
| Area | 265425 | ft² |  | Manual Input | [12 empty] | kW | [6 empty] | 0 | kBtu/ft²
[5 empty] | Value Used | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | kWh | kWh | kWh
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed Case 3
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand |  |  | Renewable Energy Generation |  |  |  | Energy Results
| Select Case |  |  |  | Imported Data | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | PV | Wind | SolarHW |  | Total | 0 | kBtu
| Area | 265425 | ft² |  | Manual Input | [12 empty] | kW | [6 empty] | 0 | kBtu/ft²
[5 empty] | Value Used | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | kWh | kWh | kWh
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed Case 4
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand |  |  | Renewable Energy Generation |  |  |  | Energy Results
| Select Case |  |  |  | Imported Data | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | PV | Wind | SolarHW |  | Total | 0 | kBtu
| Area | 265425 | ft² |  | Manual Input | [12 empty] | kW | [6 empty] | 0 | kBtu/ft²
[5 empty] | Value Used | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | kWh | kWh | kWh
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed Case 5
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand |  |  | Renewable Energy Generation |  |  |  | Energy Results
| Select Case |  |  |  | Imported Data | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | PV | Wind | SolarHW |  | Total | 0 | kBtu
| Area | 265425 | ft² |  | Manual Input | [12 empty] | kW | [6 empty] | 0 | kBtu/ft²
[5 empty] | Value Used | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | kWh | kWh | kWh
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed Case 6
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand |  |  | Renewable Energy Generation |  |  |  | Energy Results
| Select Case |  |  |  | Imported Data | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | PV | Wind | SolarHW |  | Total | 0 | kBtu
| Area | 265425 | ft² |  | Manual Input | [12 empty] | kW | [6 empty] | 0 | kBtu/ft²
[5 empty] | Value Used | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | kWh | kWh | kWh
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed Case 7
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand |  |  | Renewable Energy Generation |  |  |  | Energy Results
| Select Case |  |  |  | Imported Data | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | PV | Wind | SolarHW |  | Total | 0 | kBtu
| Area | 265425 | ft² |  | Manual Input | [12 empty] | kW | [6 empty] | 0 | kBtu/ft²
[5 empty] | Value Used | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | kWh | kWh | kWh
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed Case 8
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand |  |  | Renewable Energy Generation |  |  |  | Energy Results
| Select Case |  |  |  | Imported Data | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | PV | Wind | SolarHW |  | Total | 0 | kBtu
| Area | 265425 | ft² |  | Manual Input | [12 empty] | kW | [6 empty] | 0 | kBtu/ft²
[5 empty] | Value Used | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | kWh | kWh | kWh
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed Case 9
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand |  |  | Renewable Energy Generation |  |  |  | Energy Results
| Select Case |  |  |  | Imported Data | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | PV | Wind | SolarHW |  | Total | 0 | kBtu
| Area | 265425 | ft² |  | Manual Input | [12 empty] | kW | [6 empty] | 0 | kBtu/ft²
[5 empty] | Value Used | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | kWh | kWh | kWh
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed Case 10
[6 empty] | Case Name |  | Result File Path and Name | [5 empty] | Timestamp |  |  | Peak Electrical Demand |  |  | Renewable Energy Generation |  |  |  | Energy Results
| Select Case |  |  |  | Imported Data | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | PV | Wind | SolarHW |  | Total | 0 | kBtu
| Area | 265425 | ft² |  | Manual Input | [12 empty] | kW | [6 empty] | 0 | kBtu/ft²
[5 empty] | Value Used | 0 |  | 0 | [5 empty] | 0 |  |  | 0 | kW |  | kWh | kWh | kWh
| End Use | Heating |  |  |  | Cooling |  | Lighting | Exterior Lighting | Equipment |  |  | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems |  |  |  | Refrigeration | Generators | 0 | 0
| Fuel Source | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Electricity
| Input Units | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu | kBtu
| Imported Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Input
| Value Used | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## SiteE
Energy Use
|  |  | Baseline (LEED or Code) | [11 empty] | LEED | Yes
| Select Cases for Comparison |  | LEED Baseline | Compliance Baseline | Proposed Design | [9 empty] | 3 | Heating | Cooling | Lighting | Exterior Lighting | Equipment | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems | Refrigeration | Generators |  |  | Uncertainty | PV | Wind | SHW | Total | Savings Target
[16 empty] | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | [9 empty] | Electricity | Gas | Additional Fuel | District Cooling | District Heating
| Energy Use Summary |  | LEED Baseline | Compliance Baseline | Proposed Design | [9 empty] | Energy Use (kBtu)
| Electricity | kBtu | 32175875 | 38329375 | 25578500 | 18650458.75 | 18650458.75 | 18650458.75 | 18650458.75 | 18650458.75 | 18650458.75 | 18650458.75 | 18650458.75 | 18650458.75 | LEED Baseline | 9658500 | 4386500 | 2580000 | 0 | 7093000 | 0 | 3874250 | 3908500 | 287425 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32175875 | 0 | 0% LEED Target | 32175875 | 32175875 | 32175875 | 0 | 0 | 0 | 0
| Gas | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compliance Baseline | 10422500 | 5812000 | 2487000 | 0 | 7093000 | 0 | 7611500 | 4183500 | 332175 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38329375 | 0 | 0% Code Target | 38329375 | 38329375 | 38329375 | 0 | 0 | 0 | 0
| Additional Fuel | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Proposed Design | 1397000 | 3678000 | 1758000 | 0 | 7104000 | 0 | 10080000 | 1066000 | 0 | 0 | 0 | 495500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25578500 |  |  |  |  | 25578500 | 0 | 0 | 0 | 0
| District Cooling | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3856325 | 2150440 | 920190 | 0 | 7093000 | 0 | 2816255 | 1547895 | 122904.75 | 0 | 0 | 143449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18650458.75 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| District Heating | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3856325 | 2150440 | 920190 | 0 | 7093000 | 0 | 2816255 | 1547895 | 122904.75 | 0 | 0 | 143449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18650458.75 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| Total | kBtu | 32175875 | 38329375 | 25578500 | 18650458.75 | 18650458.75 | 18650458.75 | 18650458.75 | 18650458.75 | 18650458.75 | 18650458.75 | 18650458.75 | 18650458.75 |  | 3856325 | 2150440 | 920190 | 0 | 7093000 | 0 | 2816255 | 1547895 | 122904.75 | 0 | 0 | 143449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18650458.75 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| Energy Use Intensity | kBtu/ft² | 121.224 | 144.4076 | 96.3681 | 70.2664 | 70.2664 | 70.2664 | 70.2664 | 70.2664 | 70.2664 | 70.2664 | 70.2664 | 70.2664 |  | 3856325 | 2150440 | 920190 | 0 | 7093000 | 0 | 2816255 | 1547895 | 122904.75 | 0 | 0 | 143449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18650458.75 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| Energy Use Savings | % |  | -19.12% | 20.5% | [10 empty] | 3856325 | 2150440 | 920190 | 0 | 7093000 | 0 | 2816255 | 1547895 | 122904.75 | 0 | 0 | 143449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18650458.75 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
[16 empty] | 3856325 | 2150440 | 920190 | 0 | 7093000 | 0 | 2816255 | 1547895 | 122904.75 | 0 | 0 | 143449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18650458.75 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
[16 empty] | 3856325 | 2150440 | 920190 | 0 | 7093000 | 0 | 2816255 | 1547895 | 122904.75 | 0 | 0 | 143449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18650458.75 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Energy Use Intensity (kBtu/ft²)
[15 empty] | LEED Baseline | 36.3888 | 16.5263 | 9.7203 | 0 | 26.7232 | 0 | 14.5964 | 14.7254 | 1.0829 | 0 | 0 | 1.4607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.224 | 0 | 0% LEED Target | 121.224 | 121.224 | 121.224 | 0 | 0 | 0 | 0
[15 empty] | Compliance Baseline | 39.2672 | 21.897 | 9.3699 | 0 | 26.7232 | 0 | 28.6767 | 15.7615 | 1.2515 | 0 | 0 | 1.4607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144.4076 | 0 | 0% Code Target | 144.4076 | 144.4076 | 144.4076 | 0 | 0 | 0 | 0
[15 empty] | Proposed Design | 5.2633 | 13.857 | 6.6233 | 0 | 26.7646 | 0 | 37.9768 | 4.0162 | 0 | 0 | 0 | 1.8668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.3681 |  |  |  |  | 96.3681 | 0 | 0 | 0 | 0
[16 empty] | 14.5289 | 8.1019 | 3.4669 | 0 | 26.7232 | 0 | 10.6104 | 5.8318 | 0.46305 | 0 | 0 | 0.54045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2664 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 14.5289 | 8.1019 | 3.4669 | 0 | 26.7232 | 0 | 10.6104 | 5.8318 | 0.46305 | 0 | 0 | 0.54045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2664 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 14.5289 | 8.1019 | 3.4669 | 0 | 26.7232 | 0 | 10.6104 | 5.8318 | 0.46305 | 0 | 0 | 0.54045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2664 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 14.5289 | 8.1019 | 3.4669 | 0 | 26.7232 | 0 | 10.6104 | 5.8318 | 0.46305 | 0 | 0 | 0.54045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2664 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 14.5289 | 8.1019 | 3.4669 | 0 | 26.7232 | 0 | 10.6104 | 5.8318 | 0.46305 | 0 | 0 | 0.54045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2664 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 14.5289 | 8.1019 | 3.4669 | 0 | 26.7232 | 0 | 10.6104 | 5.8318 | 0.46305 | 0 | 0 | 0.54045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2664 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 14.5289 | 8.1019 | 3.4669 | 0 | 26.7232 | 0 | 10.6104 | 5.8318 | 0.46305 | 0 | 0 | 0.54045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2664 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 14.5289 | 8.1019 | 3.4669 | 0 | 26.7232 | 0 | 10.6104 | 5.8318 | 0.46305 | 0 | 0 | 0.54045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2664 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 14.5289 | 8.1019 | 3.4669 | 0 | 26.7232 | 0 | 10.6104 | 5.8318 | 0.46305 | 0 | 0 | 0.54045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2664 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0

## SourceE
Source Energy Use
[15 empty] | LEED | Yes
[15 empty] | 3 | Heating | Cooling | Lighting | Exterior Lighting | Equipment | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems | Refrigeration | Generators |  |  | Uncertainty | PV | Wind | SHW | Total | Savings Target
[16 empty] | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | [9 empty] | Electricity | Gas | Additional Fuel | District Cooling | District Heating
| Source Energy Use Summary |  | LEED Baseline | Compliance Baseline | Proposed Design | [9 empty] | Source Energy Use (kBtu)
| Electricity | kBtu | 90092450 | 107322250 | 71619800 | 52221284.5 | 52221284.5 | 52221284.5 | 52221284.5 | 52221284.5 | 52221284.5 | 52221284.5 | 52221284.5 | 52221284.5 | LEED Baseline | 27043800 | 12282200 | 7224000 | 0 | 19860400 | 0 | 10847900 | 10943800 | 804790 | 0 | 0 | 1085560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90092450 | 0 | 0% LEED Target | 32175875 | 32175875 | 32175875 | 0 | 0 | 0 | 0
| Gas | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compliance Baseline | 29183000 | 16273600 | 6963600 | 0 | 19860400 | 0 | 21312200 | 11713800 | 930090 | 0 | 0 | 1085560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107322250 | 0 | 0% Code Target | 38329375 | 38329375 | 38329375 | 0 | 0 | 0 | 0
| Additional Fuel | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Proposed Design | 3911600 | 10298400 | 4922400 | 0 | 19891200 | 0 | 28224000 | 2984800 | 0 | 0 | 0 | 1387400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71619800 |  |  |  |  | 25578500 | 0 | 0 | 0 | 0
| District Cooling | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10797710 | 6021232 | 2576532 | 0 | 19860400 | 0 | 7885514 | 4334106 | 344133.3 | 0 | 0 | 401657.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52221284.5 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| District Heating | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10797710 | 6021232 | 2576532 | 0 | 19860400 | 0 | 7885514 | 4334106 | 344133.3 | 0 | 0 | 401657.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52221284.5 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| Total | kBtu | 90092450 | 107322250 | 71619800 | 52221284.5 | 52221284.5 | 52221284.5 | 52221284.5 | 52221284.5 | 52221284.5 | 52221284.5 | 52221284.5 | 52221284.5 |  | 10797710 | 6021232 | 2576532 | 0 | 19860400 | 0 | 7885514 | 4334106 | 344133.3 | 0 | 0 | 401657.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52221284.5 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| Source Energy Use Intensity | kBtu/ft² | 339.4271 | 404.3412 | 269.8306 | 196.7459 | 196.7459 | 196.7459 | 196.7459 | 196.7459 | 196.7459 | 196.7459 | 196.7459 | 196.7459 |  | 10797710 | 6021232 | 2576532 | 0 | 19860400 | 0 | 7885514 | 4334106 | 344133.3 | 0 | 0 | 401657.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52221284.5 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| Source Energy Use Savings | % |  | -19.12% | 20.5% | [10 empty] | 10797710 | 6021232 | 2576532 | 0 | 19860400 | 0 | 7885514 | 4334106 | 344133.3 | 0 | 0 | 401657.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52221284.5 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
|  |  |  | 0 | [11 empty] | 10797710 | 6021232 | 2576532 | 0 | 19860400 | 0 | 7885514 | 4334106 | 344133.3 | 0 | 0 | 401657.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52221284.5 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
[16 empty] | 10797710 | 6021232 | 2576532 | 0 | 19860400 | 0 | 7885514 | 4334106 | 344133.3 | 0 | 0 | 401657.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52221284.5 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
[15 empty] | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
[15 empty] | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Source Energy Use Intensity (kBtu/ft²)
[15 empty] | LEED Baseline | 101.8887 | 46.2737 | 27.2167 | 0 | 74.8249 | 0 | 40.8699 | 41.2312 | 3.0321 | 0 | 0 | 4.0899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339.4271 | 0 | 0% LEED Target | 121.224 | 121.224 | 121.224 | 0 | 0 | 0 | 0
[15 empty] | Compliance Baseline | 109.9482 | 61.3115 | 26.2357 | 0 | 74.8249 | 0 | 80.2946 | 44.1322 | 3.5042 | 0 | 0 | 4.0899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404.3412 | 0 | 0% Code Target | 144.4076 | 144.4076 | 144.4076 | 0 | 0 | 0 | 0
[15 empty] | Proposed Design | 14.7371 | 38.7997 | 18.5454 | 0 | 74.9409 | 0 | 106.3351 | 11.2454 | 0 | 0 | 0 | 5.2271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269.8306 |  |  |  |  | 96.3681 | 0 | 0 | 0 | 0
[16 empty] | 40.6808 | 22.6852 | 9.7072 | 0 | 74.8249 | 0 | 29.709 | 16.3289 | 1.2965 | 0 | 0 | 1.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.7459 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 40.6808 | 22.6852 | 9.7072 | 0 | 74.8249 | 0 | 29.709 | 16.3289 | 1.2965 | 0 | 0 | 1.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.7459 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 40.6808 | 22.6852 | 9.7072 | 0 | 74.8249 | 0 | 29.709 | 16.3289 | 1.2965 | 0 | 0 | 1.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.7459 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 40.6808 | 22.6852 | 9.7072 | 0 | 74.8249 | 0 | 29.709 | 16.3289 | 1.2965 | 0 | 0 | 1.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.7459 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 40.6808 | 22.6852 | 9.7072 | 0 | 74.8249 | 0 | 29.709 | 16.3289 | 1.2965 | 0 | 0 | 1.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.7459 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 40.6808 | 22.6852 | 9.7072 | 0 | 74.8249 | 0 | 29.709 | 16.3289 | 1.2965 | 0 | 0 | 1.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.7459 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 40.6808 | 22.6852 | 9.7072 | 0 | 74.8249 | 0 | 29.709 | 16.3289 | 1.2965 | 0 | 0 | 1.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.7459 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 40.6808 | 22.6852 | 9.7072 | 0 | 74.8249 | 0 | 29.709 | 16.3289 | 1.2965 | 0 | 0 | 1.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.7459 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 40.6808 | 22.6852 | 9.7072 | 0 | 74.8249 | 0 | 29.709 | 16.3289 | 1.2965 | 0 | 0 | 1.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.7459 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0

## Carbon
Carbon Emissions
[15 empty] | LEED | Yes
[15 empty] | 3 | Heating | Cooling | Lighting | Exterior Lighting | Equipment | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems | Refrigeration | Generators |  |  | Uncertainty | PV | Wind | SHW | Total | Savings Target
[16 empty] | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | [9 empty] | Electricity | Gas | Additional Fuel | District Cooling | District Heating
| Carbon Emissions Summary |  | LEED Baseline | Compliance Baseline | Proposed Design | [9 empty] | Carbon Emissions (kg CO2e)
| Electricity | kg CO2e | 4384867.5245 | 5223454.8919 | 3485789.7097 | 5223454.8919 | 5223454.8919 | 5223454.8919 | 5223454.8919 | 5223454.8919 | 5223454.8919 | 5223454.8919 | 5223454.8919 | 5223454.8919 | LEED Baseline | 1316242.153 | 597783.942 | 351597.5312 | 0 | 966620.6545 | 0 | 527975.4787 | 532643.0041 | 39169.7366 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4384867.5245 | 0 | 0% LEED Target | 4384867.5245 | 4384867.5245 | 4384867.5245 | 0 | 0 | 0 | 0
| Gas | kg CO2e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compliance Baseline | 1420358.6312 | 792048.3919 | 338923.6667 | 0 | 966620.6545 | 0 | 1037280.856 | 570119.4851 | 45268.1821 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5223454.8919 | 0 | 0% Code Target | 5223454.8919 | 5223454.8919 | 5223454.8919 | 0 | 0 | 0 | 0
| Additional Fuel | kg CO2e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Proposed Design | 190380.5237 | 501230.8991 | 239576.9224 | 0 | 968119.7137 | 0 | 1373683.3776 | 145272.4683 | 0 | 0 | 0 | 67525.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3485789.7097 |  |  |  |  | 3485789.7097 | 0 | 0 | 0 | 0
| District Cooling | kg CO2e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1420358.6312 | 792048.3919 | 338923.6667 | 0 | 966620.6545 | 0 | 1037280.856 | 570119.4851 | 45268.1821 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5223454.8919 |  |  |  |  | 5223454.8919 | 0 | 0 | 0 | 0
| District Heating | kg CO2e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1420358.6312 | 792048.3919 | 338923.6667 | 0 | 966620.6545 | 0 | 1037280.856 | 570119.4851 | 45268.1821 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5223454.8919 |  |  |  |  | 5223454.8919 | 0 | 0 | 0 | 0
| Total | kg CO2e | 4384867.5245 | 5223454.8919 | 3485789.7097 | 5223454.8919 | 5223454.8919 | 5223454.8919 | 5223454.8919 | 5223454.8919 | 5223454.8919 | 5223454.8919 | 5223454.8919 | 5223454.8919 |  | 1420358.6312 | 792048.3919 | 338923.6667 | 0 | 966620.6545 | 0 | 1037280.856 | 570119.4851 | 45268.1821 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5223454.8919 |  |  |  |  | 5223454.8919 | 0 | 0 | 0 | 0
| Carbon Emissions Intensity | kg CO2e/ft² | 16.5202 | 19.6796 | 13.1329 | 19.6796 | 19.6796 | 19.6796 | 19.6796 | 19.6796 | 19.6796 | 19.6796 | 19.6796 | 19.6796 |  | 1420358.6312 | 792048.3919 | 338923.6667 | 0 | 966620.6545 | 0 | 1037280.856 | 570119.4851 | 45268.1821 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5223454.8919 |  |  |  |  | 5223454.8919 | 0 | 0 | 0 | 0
| Carbon Emissions Savings | % |  | -19.12% | 20.5% | [10 empty] | 1420358.6312 | 792048.3919 | 338923.6667 | 0 | 966620.6545 | 0 | 1037280.856 | 570119.4851 | 45268.1821 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5223454.8919 |  |  |  |  | 5223454.8919 | 0 | 0 | 0 | 0
[16 empty] | 1420358.6312 | 792048.3919 | 338923.6667 | 0 | 966620.6545 | 0 | 1037280.856 | 570119.4851 | 45268.1821 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5223454.8919 |  |  |  |  | 5223454.8919 | 0 | 0 | 0 | 0
[16 empty] | 1420358.6312 | 792048.3919 | 338923.6667 | 0 | 966620.6545 | 0 | 1037280.856 | 570119.4851 | 45268.1821 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5223454.8919 |  |  |  |  | 5223454.8919 | 0 | 0 | 0 | 0
[15 empty] | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
[15 empty] | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Carbon Emissions Intensity (kg CO2e/ft²)
[15 empty] | LEED Baseline | 4.959 | 2.2522 | 1.3247 | 0 | 3.6418 | 0 | 1.9892 | 2.0068 | 0.14757 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5202 | 0 | 0% LEED Target | 16.5202 | 16.5202 | 121.224 | 0 | 0 | 0 | 0
[15 empty] | Compliance Baseline | 5.3513 | 2.9841 | 1.2769 | 0 | 3.6418 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6796 | 0 | 0% Code Target | 19.6796 | 19.6796 | 144.4076 | 0 | 0 | 0 | 0
[15 empty] | Proposed Design | 0.71727 | 1.8884 | 0.90262 | 0 | 3.6474 | 0 | 5.1754 | 0.54732 | 0 | 0 | 0 | 0.25441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.1329 |  |  |  |  | 96.3681 | 0 | 0 | 0 | 0
[16 empty] | 5.3513 | 2.9841 | 1.2769 | 0 | 3.6418 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6796 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 5.3513 | 2.9841 | 1.2769 | 0 | 3.6418 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6796 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 5.3513 | 2.9841 | 1.2769 | 0 | 3.6418 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6796 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 5.3513 | 2.9841 | 1.2769 | 0 | 3.6418 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6796 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 5.3513 | 2.9841 | 1.2769 | 0 | 3.6418 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6796 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 5.3513 | 2.9841 | 1.2769 | 0 | 3.6418 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6796 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 5.3513 | 2.9841 | 1.2769 | 0 | 3.6418 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6796 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 5.3513 | 2.9841 | 1.2769 | 0 | 3.6418 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6796 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 5.3513 | 2.9841 | 1.2769 | 0 | 3.6418 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6796 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0

## Cost
Energy Cost
[15 empty] | LEED | Yes
[15 empty] | 3 | Heating | Cooling | Lighting | Exterior Lighting | Equipment | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems | Refrigeration | Generators |  |  | Uncertainty | PV | Wind | SHW | Total | Savings Target
[16 empty] | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | [9 empty] | Electricity | Gas | Additional Fuel | District Cooling | District Heating
| Energy Cost Summary |  | LEED Baseline | Compliance Baseline | Proposed Design | [9 empty] | Energy Cost ($)
| Electricity | $ | 1367324.2818 | 1628819.2674 | 1086966.6837 | 792557.3156 | 792557.3156 | 792557.3156 | 792557.3156 | 792557.3156 | 792557.3156 | 792557.3156 | 792557.3156 | 792557.3156 | LEED Baseline | 410441.1015 | 186405.7454 | 109637.9398 | 0 | 301419.3439 | 0 | 164637.5149 | 166092.9798 | 12214.2189 | 0 | 0 | 16475.4377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1367324.2818 | 0 | 0% LEED Target | 1367324.2818 | 1367324.2818 | 32175875 | 0 | 0 | 0 | 0
| Gas | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compliance Baseline | 442907.5302 | 246982.8319 | 105685.8746 | 0 | 301419.3439 | 0 | 323453.1702 | 177779.1943 | 14115.8848 | 0 | 0 | 16475.4377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1628819.2674 | 0 | 0% Code Target | 1628819.2674 | 1628819.2674 | 38329375 | 0 | 0 | 0 | 0
| Additional Fuel | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Proposed Design | 59365.9697 | 156297.8072 | 74706.7823 | 0 | 301886.7925 | 0 | 428352.8812 | 45300.017 | 0 | 0 | 0 | 21056.4338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1086966.6837 |  |  |  |  | 25578500 | 0 | 0 | 0 | 0
| District Cooling | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 163875.7862 | 91383.6478 | 39103.7736 | 0 | 301419.3439 | 0 | 119677.673 | 65778.3019 | 5222.8774 | 0 | 0 | 6095.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792557.3156 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| District Heating | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 163875.7862 | 91383.6478 | 39103.7736 | 0 | 301419.3439 | 0 | 119677.673 | 65778.3019 | 5222.8774 | 0 | 0 | 6095.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792557.3156 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| Total | $ | 1367324.2818 | 1628819.2674 | 1086966.6837 | 792557.3156 | 792557.3156 | 792557.3156 | 792557.3156 | 792557.3156 | 792557.3156 | 792557.3156 | 792557.3156 | 792557.3156 |  | 163875.7862 | 91383.6478 | 39103.7736 | 0 | 301419.3439 | 0 | 119677.673 | 65778.3019 | 5222.8774 | 0 | 0 | 6095.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792557.3156 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| Energy Cost Intensity | $/ft² | 5.1515 | 6.1366 | 4.0952 | 2.986 | 2.986 | 2.986 | 2.986 | 2.986 | 2.986 | 2.986 | 2.986 | 2.986 |  | 163875.7862 | 91383.6478 | 39103.7736 | 0 | 301419.3439 | 0 | 119677.673 | 65778.3019 | 5222.8774 | 0 | 0 | 6095.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792557.3156 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| Energy Cost Savings | % |  | -19.12% | 20.5% | [10 empty] | 163875.7862 | 91383.6478 | 39103.7736 | 0 | 301419.3439 | 0 | 119677.673 | 65778.3019 | 5222.8774 | 0 | 0 | 6095.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792557.3156 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
| LEED Points |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 163875.7862 | 91383.6478 | 39103.7736 | 0 | 301419.3439 | 0 | 119677.673 | 65778.3019 | 5222.8774 | 0 | 0 | 6095.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792557.3156 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
[16 empty] | 163875.7862 | 91383.6478 | 39103.7736 | 0 | 301419.3439 | 0 | 119677.673 | 65778.3019 | 5222.8774 | 0 | 0 | 6095.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792557.3156 |  |  |  |  | 18650458.75 | 0 | 0 | 0 | 0
[15 empty] | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
[15 empty] | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Energy Cost Intensity ($/ft²)
[15 empty] | LEED Baseline | 1.5464 | 0.70229 | 0.41307 | 0 | 1.1356 | 0 | 0.62028 | 0.62576 | 0.046018 | 0 | 0 | 0.062072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1515 | 0 | 0% LEED Target | 5.1515 | 5.1515 | 121.224 | 0 | 0 | 0 | 0
[15 empty] | Compliance Baseline | 1.6687 | 0.93052 | 0.39818 | 0 | 1.1356 | 0 | 1.2186 | 0.66979 | 0.053182 | 0 | 0 | 0.062072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1366 | 0 | 0% Code Target | 6.1366 | 6.1366 | 144.4076 | 0 | 0 | 0 | 0
[15 empty] | Proposed Design | 0.22366 | 0.58886 | 0.28146 | 0 | 1.1374 | 0 | 1.6138 | 0.17067 | 0 | 0 | 0 | 0.079331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0952 |  |  |  |  | 96.3681 | 0 | 0 | 0 | 0
[16 empty] | 0.61741 | 0.34429 | 0.14733 | 0 | 1.1356 | 0 | 0.45089 | 0.24782 | 0.019677 | 0 | 0 | 0.022967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.986 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 0.61741 | 0.34429 | 0.14733 | 0 | 1.1356 | 0 | 0.45089 | 0.24782 | 0.019677 | 0 | 0 | 0.022967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.986 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 0.61741 | 0.34429 | 0.14733 | 0 | 1.1356 | 0 | 0.45089 | 0.24782 | 0.019677 | 0 | 0 | 0.022967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.986 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 0.61741 | 0.34429 | 0.14733 | 0 | 1.1356 | 0 | 0.45089 | 0.24782 | 0.019677 | 0 | 0 | 0.022967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.986 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 0.61741 | 0.34429 | 0.14733 | 0 | 1.1356 | 0 | 0.45089 | 0.24782 | 0.019677 | 0 | 0 | 0.022967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.986 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 0.61741 | 0.34429 | 0.14733 | 0 | 1.1356 | 0 | 0.45089 | 0.24782 | 0.019677 | 0 | 0 | 0.022967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.986 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 0.61741 | 0.34429 | 0.14733 | 0 | 1.1356 | 0 | 0.45089 | 0.24782 | 0.019677 | 0 | 0 | 0.022967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.986 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 0.61741 | 0.34429 | 0.14733 | 0 | 1.1356 | 0 | 0.45089 | 0.24782 | 0.019677 | 0 | 0 | 0.022967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.986 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0
[16 empty] | 0.61741 | 0.34429 | 0.14733 | 0 | 1.1356 | 0 | 0.45089 | 0.24782 | 0.019677 | 0 | 0 | 0.022967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.986 |  |  |  |  | 70.2664 | 0 | 0 | 0 | 0

## Report
Energy Report Result Summary Tables
[13 empty] | Energy Use | [7 empty] | Source Energy Use | [8 empty] | Carbon Emissions | [8 empty] | Energy Cost
| Proposed Design Scenario | Proposed Design |  |  | Energy Use | [6 empty] | Energy Demand by End Use |  | Source Energy Use | [7 empty] | Carbon Emissions | [6 empty] | Carbon Demand by End Use |  | Energy Cost | [6 empty] | Cost Demand by End Use
| Building Performance Summary | Units |  |  | End Use | Units | LEED Baseline | Code Baseline | Proposed | LEED | Code |  |  | End Use | Units | LEED Baseline | Code Baseline | Proposed | LEED | Code |  | End Use | Units | LEED Baseline | Code Baseline | Proposed | LEED | Code |  |  | End Use |  | LEED Baseline | Code Baseline | Proposed | LEED | Code |  |  |  | LEED Baseline | Code Baseline | Proposed | Header | LEED Baseline Row | Code Baseline Row | Proposed Row | Column
| Energy Use Intensity (EUI) | kBtu/ft² | 96.3681 |  | Heating | kBtu | 9658500 | 10422500 | 1397000 | 85.54% | 86.6% |  |  | Heating | kBtu | 27043800 | 29183000 | 3911600 | 94.83% | 95.21% |  | Heating | kg CO2e | 1316242.153 | 1420358.6312 | 190380.5237 | 85.54% | 86.6% |  |  | Heating | $/yr | 410441.1015 | 442907.5302 | 59365.9697 | 85.54% | 86.6% |  |  | Unmet Heating Hours | 1342 | 1339 | 1076 | Heating Unmet Hours | 2 | 6 | 2 | 6
| Carbon Emissions Intensity (CEI) | kg CO2e/ft² | 13.1329 |  | Cooling | kBtu | 4386500 | 5812000 | 3678000 | 16.15% | 36.72% |  |  | Cooling | kBtu | 12282200 | 16273600 | 10298400 | 70.05% | 77.4% |  | Cooling | kg CO2e | 597783.942 | 792048.3919 | 501230.8991 | 16.15% | 36.72% |  |  | Cooling | $/yr | 186405.7454 | 246982.8319 | 156297.8072 | 16.15% | 36.72% |  |  | Unmet Cooling Hours | 648 | 512 | 659 | Cooling Unmet Hours | 2 | 6 | 2 | 7
| Energy Cost Intensity (ECI) | $/ft² | 4.0952 | No | Lighting | kBtu | 2580000 | 2487000 | 1758000 | 31.86% | 29.31% |  |  | Lighting | kBtu | 7224000 | 6963600 | 4922400 | 75.66% | 74.75% |  | Lighting | kg CO2e | 351597.5312 | 338923.6667 | 239576.9224 | 31.86% | 29.31% |  |  | Lighting | $/yr | 109637.9398 | 105685.8746 | 74706.7823 | 31.86% | 29.31%
|  |  |  | No | Exterior Lighting | kBtu | 0 | 0 | 0 | 0% | 0% |  |  | Exterior Lighting | kBtu | 0 | 0 | 0 | 0% | 0% |  | Exterior Lighting | kg CO2e | 0 | 0 | 0 | 0% | 0% |  |  | Exterior Lighting | $/yr | 0 | 0 | 0 | 0% | 0%
|  |  |  | No | Equipment | kBtu | 7093000 | 7093000 | 7104000 | -0.1551% | -0.1551% |  |  | Equipment | kBtu | 19860400 | 19860400 | 19891200 | 64.23% | 64.23% |  | Equipment | kg CO2e | 966620.6545 | 966620.6545 | 968119.7137 | -0.1551% | -0.1551% |  |  | Equipment | $/yr | 301419.3439 | 301419.3439 | 301886.7925 | -0.1551% | -0.1551%
| LEED Energy Credit Summary | Savings | Points | No | Exterior Equipment | kBtu | 0 | 0 | 0 | 0% | 0% |  |  | Exterior Equipment | kBtu | 0 | 0 | 0 | 0% | 0% |  | Exterior Equipment | kg CO2e | 0 | 0 | 0 | 0% | 0% |  |  | Exterior Equipment | $/yr | 0 | 0 | 0 | 0% | 0%
| Optimize Energy Performance | 20.5% | 8 | Yes | Fans | kBtu | 3874250 | 7611500 | 10080000 | -160.2% | -32.43% |  |  | Fans | kBtu | 10847900 | 21312200 | 28224000 | 7.079% | 52.7% |  | Fans | kg CO2e | 527975.4787 | 1037280.856 | 1373683.3776 | -160.2% | -32.43% |  |  | Fans | $/yr | 164637.5149 | 323453.1702 | 428352.8812 | -160.2% | -32.43%
| EApc95 Alternative Metric | 20.5% | 8 | Yes | Pumps | kBtu | 3908500 | 4183500 | 1066000 | 72.73% | 74.52% |  |  | Pumps | kBtu | 10943800 | 11713800 | 2984800 | 90.26% | 90.9% |  | Pumps | kg CO2e | 532643.0041 | 570119.4851 | 145272.4683 | 72.73% | 74.52% |  |  | Pumps | $/yr | 166092.9798 | 177779.1943 | 45300.017 | 72.73% | 74.52%
| Renewable Energy Production | 0% | 0 | No | Heat Rejection | kBtu | 287425 | 332175 | 0 | 100% | 100% |  |  | Heat Rejection | kBtu | 804790 | 930090 | 0 | 100% | 100% |  | Heat Rejection | kg CO2e | 39169.7366 | 45268.1821 | 0 | 100% | 100% |  |  | Heat Rejection | $/yr | 12214.2189 | 14115.8848 | 0 | 100% | 100%
| 0 |  |  | No | Humidification | kBtu | 0 | 0 | 0 | 0% | 0% |  |  | Humidification | kBtu | 0 | 0 | 0 | 0% | 0% |  | Humidification | kg CO2e | 0 | 0 | 0 | 0% | 0% |  |  | Humidification | $/yr | 0 | 0 | 0 | 0% | 0%
| 0 |  |  | No | Heat Recovery | kBtu | 0 | 0 | 0 | 0% | 0% |  |  | Heat Recovery | kBtu | 0 | 0 | 0 | 0% | 0% |  | Heat Recovery | kg CO2e | 0 | 0 | 0 | 0% | 0% |  |  | Heat Recovery | $/yr | 0 | 0 | 0 | 0% | 0%
|  |  |  | No | Water Systems | kBtu | 387700 | 387700 | 495500 | -27.81% | -27.81% |  |  | Water Systems | kBtu | 1085560 | 1085560 | 1387400 | 54.36% | 54.36% |  | Water Systems | kg CO2e | 52835.0244 | 52835.0244 | 67525.8049 | -27.81% | -27.81% |  |  | Water Systems | $/yr | 16475.4377 | 16475.4377 | 21056.4338 | -27.81% | -27.81%
| AIA 2030 Summary |  |  | No | Refrigeration | kBtu | 0 | 0 | 0 | 0% | 0% |  |  | Refrigeration | kBtu | 0 | 0 | 0 | 0% | 0% |  | Refrigeration | kg CO2e | 0 | 0 | 0 | 0% | 0% |  |  | Refrigeration | $/yr | 0 | 0 | 0 | 0% | 0%
| Gross Conditioned Floor Area | ft² | 265425 | No | Generators | kBtu | 0 | 0 | 0 | 0% | 0% |  |  | Generators | kBtu | 0 | 0 | 0 | 0% | 0% |  | Generators | kg CO2e | 0 | 0 | 0 | 0% | 0% |  |  | Generators | $/yr | 0 | 0 | 0 | 0% | 0%
|  |  |  | Yes | 0 | kBtu | 0 | 0 | 0 | 0% | 0% |  |  | 0 | kBtu | 0 | 0 | 0 | 0% | 0% |  | 0 | kg CO2e | 0 | 0 | 0 | 0% | 0% |  |  | 0 | $/yr | 0 | 0 | 0 | 0% | 0%
| Gross pEUI (Design EUI) | kBtu/ft² | 96.3681 | No | 0 | kBtu | 0 | 0 | 0 | 0% | 0% |  |  | 0 | kBtu | 0 | 0 | 0 | 0% | 0% |  | 0 | kg CO2e | 0 | 0 | 0 | 0% | 0% |  |  | 0 | $/yr | 0 | 0 | 0 | 0% | 0%
| Net pEUI (w/renewable offset) | kBtu/ft² | 96.3681 | No | Renewable Energy | kBtu |  |  | 0 |  |  |  |  | Renewable Energy | kBtu |  |  | 0 |  |  |  | Renewable Energy | kg CO2e | [7 empty] | Renewable Energy | $/yr |  |  | 0
| AIA 2030 Benchmark EUI (BmEUI) | kBtu/ft² | 0 | Yes | Total Energy Use | kBtu | 32175875 | 38329375 | 25578500 | 20.5% | 33.27% |  |  | Total Source Energy Use | kBtu | 90092450 | 107322250 | 71619800 | 71.61% | 76.17% |  | Total Carbon Emissions | #REF! | 4384867.5245 | 5223454.8919 | 3485789.7097 | 20.5% | 33.27% |  |  | Total Energy Cost | $/yr | 1367324.2818 | 1628819.2674 | 1086966.6837 | 20.5% | 33.27%
| Target EUI based on 90% savings | kBtu/ft² | 0 |  | Energy Use Intensity | kBtu/ft² | 0 | 0 | 0 |  |  |  |  | Source Energy Use Intensity | 0 | 0 | 0 | 0 |  |  |  | Carbon Emissions Intensity | kg CO2e/ft² | 0 | 0 | 0 |  |  |  |  | Energy Cost Intensity | $/yr | 0 | 0 | 0
| pEUI Savings vs. BmEUI | % | 0% |  | Regulated Loads | kBtu |  | 31236375 | 18474500 |  | 40.86% |  |  | Regulated Loads | kBtu |  | 87461850 | 51728600 |  | 78.88% |  | Regulated Loads | #REF! |  | 4256834.2375 | 2517669.996 |  | 40.86% |  |  | Regulated Loads | $/yr |  | 1327399.9235 | 785079.8912 |  | 40.86%
| Predicted Annual Grid Electricity Use | kWh | 7496321.9563
| Predicted Annual Gas Use | Therm | 0
| Predicted District Use | kBtu | 0
| Predicted 'Other' Fossil Fuel Source | kBtu | 0
| Predicted On-Site Renewable Use | kWh | 0

## Input Summary
Energy Report Input Summary Table
Proposed Design
| Bulding Parameters | Units | [5 empty] | Utility Information | Units | Electricity | Gas | Additional Fuel | District Cooling | District Heating | Source
| Conditioned Floor Area | (ft²) |  |  | 0 |  |  | Unit CO2e Emissions | (kg CO2e/kBtu) | 0.042497 | 0.042497 | 0.042497 | 0.042497 | 0.042497 |  |  |  | Conditioned Floor Area (ft²) |  |  | 2 | 68 | Electricity Virtual Rate (kg CO2e/kBtu) | 54 | 54 | 54 | 54 | 54
| Total Floor Area | (ft²) |  |  | 265425 |  |  | Unit Energy Cost | ($/kBtu) | 0.042495 | 0.014 | 0.0023988 | 0.29307 | 0.29307 |  |  |  | Total Floor Area (ft²) |  |  | 2 | 69 | Electricity Virtual Rate ($/kBtu) | 47 | 47 | 47 | 47 | 47
| Envelope Parameters | Units |  |  | LEED Baseline | Code Baseline | Proposed | HVAC Parameters | Units | LEED Baseline | Code Baseline | Proposed |  |  |  | LEED Baseline | LEED Baseline | Header | LEED Baseline Row | Code Baseline Row | Proposed Row | Column | Header | LEED Baseline Row | Code Baseline Row | Proposed Row | Column
| Building WWR Actual | (%) |  |  | 34.8339 | 34.8339 | 34.5323 | Total Ventilation Air Flow Rate | (CFM) | 253316 | 256283 | 344150 |  |  |  | Compliance Baseline | 0 | Building WWR Actual (%) | 2 | 6 | 2 | 80 | Total Ventilation Air Flow Rate (CFM) | 2 | 6 | 2 | 117
| North WWR Actual | (%) |  |  | 38.337 | 38.337 | 36.1931 | Ventilation Air Flow Rate per Area | (CFM/ft²) | 0.95438 | 0.96556 | 1.2931 |  |  |  |  | 0 | North WWR Actual (%) | 2 | 6 | 2 | 81 | Ventilation Air Flow Rate per Area (CFM/ft²) | 2 | 6 | 2 | 118
| East WWR Actual | (%) |  |  | 37.0477 | 37.0477 | 37.0477 | Total Heating Airflow Rate | (CFM) | 253316 | 256283 | 344150 | [5 empty] | East WWR Actual (%) | 2 | 6 | 2 | 82 | Total Heating Airflow Rate (CFM) | 2 | 6 | 2 | 119
| South WWR Actual | (%) |  |  | 51.9874 | 51.9874 | 51.9874 | Heating Airflow Rate per Area | (CFM/ft²) | 0.95438 | 0.96556 | 1.2931 |  |  |  | Proposed Design | Proposed Design | South WWR Actual (%) | 2 | 6 | 2 | 83 | Heating Airflow Rate per Area (CFM/ft²) | 2 | 6 | 2 | 120
| West WWR Actual | (%) |  |  | 37.7311 | 37.7311 | 37.7311 | Total Cooling Airflow Rate | (CFM) | 253316 | 256283 | 344150 |  |  |  | 0 | 0 | West WWR Actual (%) | 2 | 6 | 2 | 84 | Total Cooling Airflow Rate (CFM) | 2 | 6 | 2 | 121
[5 empty] | 0 | 0 |  | Cooling Airflow Rate per Area | (CFM/ft²) | 0.95438 | 0.96556 | 1.2931 |  |  |  | 0 | 0 | [5 empty] | Cooling Airflow Rate per Area (CFM/ft²) | 2 | 6 | 2 | 122
| Wall U-Value | (Btu/h·ft²·F) |  |  | 0.062 | 0.118 | 0.054 | [8 empty] | 0 | 0 | Wall U-Value (Btu/h·ft²·F) | 2 | 6 | 2 | 100
| Roof U-Value | (Btu/h·ft²·F) |  |  | 0.047 | 0.061 | 0.042 | Chiller Efficiency | (COP) | 5 | 4.4053 | 2.7953 |  |  |  | 0 | 0 | Roof U-Value (Btu/h·ft²·F) | 2 | 6 | 2 | 102 | Chiller Efficiency (COP) | 2 | 6 | 2 | 123
| Exposed Floor U-Value | (Btu/h·ft²·F) |  |  | 0 | 0 | 0 | Boiler Efficiency | (COP) | 0.97992 | 0.97992 | 0.97743 |  |  |  | 0 | 0 | Exposed Floor U-Value (Btu/h·ft²·F) | 2 | 6 | 2 | 103 | Boiler Efficiency (COP) | 2 | 6 | 2 | 124
| Slab on Grade U-Value | (Btu/h·ft²·F) |  |  | 0.027 | 0.027 | 0.027 | [8 empty] | 0 | 0 | Slab on Grade U-Value (Btu/h·ft²·F) | 2 | 6 | 2 | 104
[5 empty] | 0 | 0 |  | DX Cooling Efficiency | (COP) | 0 | 0 | 0 |  |  |  | 0 | 0 | [5 empty] | DX Cooling Efficiency (COP) | 2 | 6 | 2 | 125
| Assembly U-Value | (Btu/h·ft²·F) |  |  | 0.079 | 0.105 | 0.086 | DX Heating Efficiency | (HSPF) | 0 | 0 | 0 |  |  |  | 0 | 0 | Assembly U-Value (Btu/h·ft²·F) | 2 | 6 | 2 | 105 | DX Heating Efficiency (HSPF) | 2 | 6 | 2 | 126
| Glass U-Value | (Btu/h·ft²·F) |  |  | N/A | N/A | 0.52625 | Heat Pump Cooling Efficiency | (COP) | 0 | 0 | 0 |  |  |  | 0 | 0 | Glass U-Value (Btu/h·ft²·F) | 2 | 6 | 2 | 106 | Heat Pump Cooling Efficiency (COP) | 2 | 6 | 2 | 127
| Glass SHGC |  |  |  | 0.878 | 0.878 | 0.40783 | Heat Pump Heating Efficiency | (COP) | 0 | 0 | 0 | [5 empty] | Glass SHGC | 2 | 6 | 2 | 107 | Heat Pump Heating Efficiency (COP) | 2 | 6 | 2 | 128
| Glass VLT |  |  |  | 0.9 | 0.9 | 0.51715 | [10 empty] | Glass VLT | 2 | 6 | 2 | 108
[8 empty] | Total Fan Power | (kW) | 329.33 | 919.249 | 1090.289 | [10 empty] | Total Fan Power (kW) | 2 | 6 | 2 | 129
| Vertical Weighted U-Value | (Btu/h·ft²·F) |  |  | 0.192 | 0.267 | 0.236 | Fan Power per CFM | (W/CFM) | 1.3001 | 3.5869 | 3.1681 | [5 empty] | Vertical Weighted U-Value (Btu/h·ft²·F) | 2 | 6 | 2 | 98
| Vertical Weighted R-Value | (ft²·h·F/Btu ) |  |  | 5.2083 | 3.7453 | 4.2373 | Total Pump Power | (kW) | 228.131 | 247.535 | 504.648 | [5 empty] | Vertical Weighted R-Value (ft²·h·F/Btu ) | 2 | 6 | 2 | 99 | Total Pump Power (kW) | 2 | 6 | 2 | 130
| Infiltration Rate | (CFM/ft² facade) | 75 | Pa | 0.26319 | 0.26319 | 0.26253 | Service Hot Water Thermal Efficiency | (COP) | 1 | 1 | 1 | [5 empty] | Infiltration Rate (CFM/ft² facade) | 2 | 6 | 2 | 110 | Service Hot Water Thermal Efficiency (COP) | 2 | 6 | 2 | 131
| Loads | Units |  |  | LEED Baseline | Code Baseline | Proposed | Exterior Uses | Units | LEED Baseline | Code Baseline | Proposed
| Lighting Power Density | (W/ft²) |  |  | 1.1876 | 1.1446 | 0.8073 | Exterior Lighting | (kW) | 0 | 0 | 0 | [5 empty] | Lighting Power Density (W/ft²) | 2 | 6 | 2 | 111 | Exterior Lighting (kW) | 2 | 6 | 2 | 132
| Occupant Density | (ft²/person) |  |  | 92.5148 | 92.5148 | 92.8625 | [10 empty] | Occupant Density (ft²/person) | 2 | 6 | 2 | 113
| Equipment Power Density | (W/ft²) |  |  | 2.4803 | 2.4803 | 2.4728 | [10 empty] | Equipment Power Density (W/ft²) | 2 | 6 | 2 | 115

## QAQC
QA/QC Checks
Unmet Hours
|  | LEED Baseline | Code Baseline | Proposed
Heating
Cooling
EFLHs
|  | LEED Baseline | Code Baseline | Proposed
| Lighting | 2398.8251 | 2399.0956 | 2404.455
| Exterior Lighting | 0 | 0 | 0
| Equipment | 3157.6001 | 3157.6001 | 3172.0729
| Pumps | 3447.7003 | 2426.6673 | 2709.5181
| Fans | 5021.1011 | 4953.0911 | 619.0729

## Menus
Units | Energy Units | Energy Cost Methodology | Carbon Methodology | Baseline Options | Code Standard | LEED Version | LEED Standard | LEED v2009 | LEED v4 | LEED v4 Energy Update | LEED v4.1 | LEED v5 (registered before 1/1/2028) | LEED v5 (registered after 1/1/2028)
SI | kWh | Enter Flat Rate | Enter Flat Rate | 0° Baseline Only | ASHRAE 2004/IECC 2006 | None | New Construction | New Buildings | New Construction | New Construction + Major Renovations | New Construction | New Construction | New Construction
IP | kBtu | Use Calculated Rate | Use Calculated Rate | Average of All Baselines | ASHRAE 2007/IECC 2009 | LEED v2009 | Major Renovation | Existing Building and Renovations | Major Renovation | Schools | Healthcare, Major Renovations, Core and Shell | 0 | 0
[5 empty] | ASHRAE 2010/IECC 2012 | LEED v4 | Core and Shell |  | Core and Shell | Core and Shell
Area Units | Energy Units | Energy Cost Units | Carbon Units | Baseline Type | ASHRAE 2013/IECC 2015 | LEED v4 Energy Update | 0 |  |  | Healthcare
m² | kWh | $ | kg CO2e | LEED | ASHRAE 2016/IECC 2018 | LEED v4.1
ft² | MWh | $ | kg CO2e | Code | ASHRAE 2019/IECC 2021 | LEED v5 (registered before 1/1/2028) | LEED Substandard | LEED v2009 | LEED v4 | LEED v4 Energy Update | LEED v4.1 | LEED v5 (registered before 1/1/2028) | LEED v5 (registered after 1/1/2028)
| GJ |  |  |  | ASHRAE 2022/IECC 2024 | LEED v5 (registered after 1/1/2028) | All but Healthcare + Schools | NC + Schools | All but Healthcare + Schools | All but Healthcare + Schools | All but Healthcare + Schools | All
Choices | kBtu | Energy Cost Normalized | Carbon Normalized | Result Options | Boston Stretch Code |  | Healthcare | Core and Shell | Healthcare | Healthcare | Healthcare | 0
Yes | MBtu | $/m² | kg CO2e/m² | LEED Baseline |  |  | School |  | School | School | School | 0
No | 1000 ft3 Gas | $/ft² | kg CO2e/ft² | Compliance Baseline
Therm
|  | Energy Cost Rate | Carbon Rate
| Energy Units | $/kWh | kg CO2e/kWh
| per kWh | $/kBtu | kg CO2e/kBtu
Fuel List | per MWh
Electricity | per GJ
Gas | per kBtu
Additional Fuel | per MBtu
District Cooling | per 1000 ft3 Gas
District Heating | per Therm
Options Pulldown | Categories
LEED Baseline | Energy Use
Compliance Baseline | Source Energy Use
Carbon Emissions
Proposed Design | Energy Cost
Pressue Drop Down
4
50
75

## Calculations
Calculations
End Use |  | Demand by End Use and Fuel Type | [24 empty] | Demand by End Use | [15 empty] | Demand by Fuel Type | [7 empty] | Renewable Energy | [7 empty] | Consumption After Renewables
End Use |  | Heating | Heating | Heating | Heating | Cooling | Cooling | Lighting | Exterior Lighting | Equipment | Equipment | Equipment | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems | Water Systems | Water Systems | Water Systems | Refrigeration | Generators | 0 | 0 | Heating | Cooling | Lighting | Exterior Lighting | Equipment | Exterior Equipment | Fans | Pumps | Heat Rejection | Humidification | Heat Recovery | Water Systems | Refrigeration | Generators | 0 | 0 | [8 empty] | PV | Wind | SolarHW | SolarHW | SolarHW | SolarHW | Total | % Renewable Energy
Fuel Type |  | Electricity | Gas | Additional Fuel | District Heating | Electricity | District Cooling | Electricity | Electricity | Electricity | Gas | Additional Fuel | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Electricity | Electricity | Electricity | Gas | [16 empty] | Electricity | Gas | Additional Fuel | District Cooling | District Heating | Gross Annual Total | LEED Savings | Code Savings | Electricity | Electricity | Electricity | Gas | Additional Fuel | District Heating | Annual Total |  | Electricity | Gas | Additional Fuel | District Cooling | District Heating | Net Annual Total | LEED Savings | Code Savings
Process Energy |  | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | No | No | Yes | No | No | Yes | No | No | No | No | Yes | Yes | No | No | No | No | No | No | Yes | No | No | Yes
Energy Use (kBtu) |  | Energy Unit Conversion Factor |  | 1
LEED Baseline |  | 9658500 | 0 | 0 | 0 | 4386500 | 0 | 2580000 | 0 | 7093000 | 0 | 0 | 0 | 3874250 | 3908500 | 287425 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9658500 | 4386500 | 2580000 | 0 | 7093000 | 0 | 3874250 | 3908500 | 287425 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 32175875 | 0 | 0 | 0 | 0 | 32175875 | [10 empty] | 32175875 | 0 | 0 | 0 | 0 | 32175875
Compliance Baseline |  | 10422500 | 0 | 0 | 0 | 5812000 | 0 | 2487000 | 0 | 7093000 | 0 | 0 | 0 | 7611500 | 4183500 | 332175 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10422500 | 5812000 | 2487000 | 0 | 7093000 | 0 | 7611500 | 4183500 | 332175 | 0 | 0 | 387700 | 0 | 0 | 0 | 0 | 38329375 | 0 | 0 | 0 | 0 | 38329375 | [10 empty] | 38329375 | 0 | 0 | 0 | 0 | 38329375
| 0.37 | 3856325 | 0 | 0 | 0 | 2150440 | 0 | 920190 | 0 | 7093000 | 0 | 0 | 0 | 2816255 | 1547895 | 122904.75 | 0 | 0 | 143449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3856325 | 2150440 | 920190 | 0 | 7093000 | 0 | 2816255 | 1547895 | 122904.75 | 0 | 0 | 143449 | 0 | 0 | 0 | 0 | 18650458.75 | 0 | 0 | 0 | 0 | 18650458.75 | [10 empty] | 18650458.75 | 0 | 0 | 0 | 0 | 18650458.75
Proposed Design |  | 1397000 | 0 | 0 | 0 | 3678000 | 0 | 1758000 | 0 | 7104000 | 0 | 0 | 0 | 10080000 | 1066000 | 0 | 0 | 0 | 495500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1397000 | 3678000 | 1758000 | 0 | 7104000 | 0 | 10080000 | 1066000 | 0 | 0 | 0 | 495500 | 0 | 0 | 0 | 0 | 25578500 | 0 | 0 | 0 | 0 | 25578500 | 20.5% | 33.27% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 25578500 | 0 | 0 | 0 | 0 | 25578500 | 20.5% | 33.27%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
Energy Use Intensity (kBtu/ft²)
LEED Baseline | 265425 | 36.3888 | 0 | 0 | 0 | 16.5263 | 0 | 9.7203 | 0 | 26.7232 | 0 | 0 | 0 | 14.5964 | 14.7254 | 1.0829 | 0 | 0 | 1.4607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.3888 | 16.5263 | 9.7203 | 0 | 26.7232 | 0 | 14.5964 | 14.7254 | 1.0829 | 0 | 0 | 1.4607 | 0 | 0 | 0 | 0 | 121.224 | 0 | 0 | 0 | 0 | 121.224 | [10 empty] | 121.224 | 0 | 0 | 0 | 0 | 121.224
Compliance Baseline | 265425 | 39.2672 | 0 | 0 | 0 | 21.897 | 0 | 9.3699 | 0 | 26.7232 | 0 | 0 | 0 | 28.6767 | 15.7615 | 1.2515 | 0 | 0 | 1.4607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.2672 | 21.897 | 9.3699 | 0 | 26.7232 | 0 | 28.6767 | 15.7615 | 1.2515 | 0 | 0 | 1.4607 | 0 | 0 | 0 | 0 | 144.4076 | 0 | 0 | 0 | 0 | 144.4076 | [10 empty] | 144.4076 | 0 | 0 | 0 | 0 | 144.4076
| 265425 | 14.5289 | 0 | 0 | 0 | 8.1019 | 0 | 3.4669 | 0 | 26.7232 | 0 | 0 | 0 | 10.6104 | 5.8318 | 0.46305 | 0 | 0 | 0.54045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5289 | 8.1019 | 3.4669 | 0 | 26.7232 | 0 | 10.6104 | 5.8318 | 0.46305 | 0 | 0 | 0.54045 | 0 | 0 | 0 | 0 | 70.2664 | 0 | 0 | 0 | 0 | 70.2664 | [10 empty] | 70.2664 | 0 | 0 | 0 | 0 | 70.2664
Proposed Design | 265425 | 5.2633 | 0 | 0 | 0 | 13.857 | 0 | 6.6233 | 0 | 26.7646 | 0 | 0 | 0 | 37.9768 | 4.0162 | 0 | 0 | 0 | 1.8668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2633 | 13.857 | 6.6233 | 0 | 26.7646 | 0 | 37.9768 | 4.0162 | 0 | 0 | 0 | 1.8668 | 0 | 0 | 0 | 0 | 96.3681 | 0 | 0 | 0 | 0 | 96.3681 | 20.5% | 33.27% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 96.3681 | 0 | 0 | 0 | 0 | 96.3681 | 20.5% | 33.27%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
Source Energy Use (kBtu)
LEED Baseline |  | 27043800 | 0 | 0 | 0 | 12282200 | 0 | 7224000 | 0 | 19860400 | 0 | 0 | 0 | 10847900 | 10943800 | 804790 | 0 | 0 | 1085560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27043800 | 12282200 | 7224000 | 0 | 19860400 | 0 | 10847900 | 10943800 | 804790 | 0 | 0 | 1085560 | 0 | 0 | 0 | 0 | 90092450 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 90092450 | 0 | 0 | 0 | 0 | 90092450
Compliance Baseline |  | 29183000 | 0 | 0 | 0 | 16273600 | 0 | 6963600 | 0 | 19860400 | 0 | 0 | 0 | 21312200 | 11713800 | 930090 | 0 | 0 | 1085560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29183000 | 16273600 | 6963600 | 0 | 19860400 | 0 | 21312200 | 11713800 | 930090 | 0 | 0 | 1085560 | 0 | 0 | 0 | 0 | 107322250 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 107322250 | 0 | 0 | 0 | 0 | 107322250
|  | 10797710 | 0 | 0 | 0 | 6021232 | 0 | 2576532 | 0 | 19860400 | 0 | 0 | 0 | 7885514 | 4334106 | 344133.3 | 0 | 0 | 401657.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10797710 | 6021232 | 2576532 | 0 | 19860400 | 0 | 7885514 | 4334106 | 344133.3 | 0 | 0 | 401657.2 | 0 | 0 | 0 | 0 | 52221284.5 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 52221284.5 | 0 | 0 | 0 | 0 | 52221284.5
Proposed Design |  | 3911600 | 0 | 0 | 0 | 10298400 | 0 | 4922400 | 0 | 19891200 | 0 | 0 | 0 | 28224000 | 2984800 | 0 | 0 | 0 | 1387400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3911600 | 10298400 | 4922400 | 0 | 19891200 | 0 | 28224000 | 2984800 | 0 | 0 | 0 | 1387400 | 0 | 0 | 0 | 0 | 71619800 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 71619800 | 0 | 0 | 0 | 0 | 71619800 | 20.5% | 33.27%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
Source Energy Use Intensity (kBtu/ft²)
LEED Baseline | 265425 | 101.8887 | 0 | 0 | 0 | 46.2737 | 0 | 27.2167 | 0 | 74.8249 | 0 | 0 | 0 | 40.8699 | 41.2312 | 3.0321 | 0 | 0 | 4.0899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8887 | 46.2737 | 27.2167 | 0 | 74.8249 | 0 | 40.8699 | 41.2312 | 3.0321 | 0 | 0 | 4.0899 | 0 | 0 | 0 | 0 | 339.4271 | 0 | 0 | 0 | 0 | 339.4271 | [10 empty] | 339.4271 | 0 | 0 | 0 | 0 | 339.4271
Compliance Baseline | 265425 | 109.9482 | 0 | 0 | 0 | 61.3115 | 0 | 26.2357 | 0 | 74.8249 | 0 | 0 | 0 | 80.2946 | 44.1322 | 3.5042 | 0 | 0 | 4.0899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.9482 | 61.3115 | 26.2357 | 0 | 74.8249 | 0 | 80.2946 | 44.1322 | 3.5042 | 0 | 0 | 4.0899 | 0 | 0 | 0 | 0 | 404.3412 | 0 | 0 | 0 | 0 | 404.3412 | [10 empty] | 404.3412 | 0 | 0 | 0 | 0 | 404.3412
| 265425 | 40.6808 | 0 | 0 | 0 | 22.6852 | 0 | 9.7072 | 0 | 74.8249 | 0 | 0 | 0 | 29.709 | 16.3289 | 1.2965 | 0 | 0 | 1.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6808 | 22.6852 | 9.7072 | 0 | 74.8249 | 0 | 29.709 | 16.3289 | 1.2965 | 0 | 0 | 1.5133 | 0 | 0 | 0 | 0 | 196.7459 | 0 | 0 | 0 | 0 | 196.7459 | [10 empty] | 196.7459 | 0 | 0 | 0 | 0 | 196.7459
Proposed Design | 265425 | 14.7371 | 0 | 0 | 0 | 38.7997 | 0 | 18.5454 | 0 | 74.9409 | 0 | 0 | 0 | 106.3351 | 11.2454 | 0 | 0 | 0 | 5.2271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7371 | 38.7997 | 18.5454 | 0 | 74.9409 | 0 | 106.3351 | 11.2454 | 0 | 0 | 0 | 5.2271 | 0 | 0 | 0 | 0 | 269.8306 | 0 | 0 | 0 | 0 | 269.8306 | 20.5% | 33.27% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 269.8306 | 0 | 0 | 0 | 0 | 269.8306 | 20.5% | 33.27%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
Carbon Emissions (kg CO2e)
LEED Baseline |  | 1316242.153 | 0 | 0 | 0 | 597783.942 | 0 | 351597.5312 | 0 | 966620.6545 | 0 | 0 | 0 | 527975.4787 | 532643.0041 | 39169.7366 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1316242.153 | 597783.942 | 351597.5312 | 0 | 966620.6545 | 0 | 527975.4787 | 532643.0041 | 39169.7366 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 4384867.5245 | 0 | 0 | 0 | 0 | 4384867.5245 | [10 empty] | 4384867.5245 | 0 | 0 | 0 | 0 | 4384867.5245
Compliance Baseline |  | 1420358.6312 | 0 | 0 | 0 | 792048.3919 | 0 | 338923.6667 | 0 | 966620.6545 | 0 | 0 | 0 | 1037280.856 | 570119.4851 | 45268.1821 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1420358.6312 | 792048.3919 | 338923.6667 | 0 | 966620.6545 | 0 | 1037280.856 | 570119.4851 | 45268.1821 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 5223454.8919 | 0 | 0 | 0 | 0 | 5223454.8919 | [10 empty] | 5223454.8919 | 0 | 0 | 0 | 0 | 5223454.8919
|  | 1420358.6312 | 0 | 0 | 0 | 792048.3919 | 0 | 338923.6667 | 0 | 966620.6545 | 0 | 0 | 0 | 1037280.856 | 570119.4851 | 45268.1821 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1420358.6312 | 792048.3919 | 338923.6667 | 0 | 966620.6545 | 0 | 1037280.856 | 570119.4851 | 45268.1821 | 0 | 0 | 52835.0244 | 0 | 0 | 0 | 0 | 5223454.8919 | 0 | 0 | 0 | 0 | 5223454.8919 | [10 empty] | 5223454.8919 | 0 | 0 | 0 | 0 | 5223454.8919
Proposed Design |  | 190380.5237 | 0 | 0 | 0 | 501230.8991 | 0 | 239576.9224 | 0 | 968119.7137 | 0 | 0 | 0 | 1373683.3776 | 145272.4683 | 0 | 0 | 0 | 67525.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190380.5237 | 501230.8991 | 239576.9224 | 0 | 968119.7137 | 0 | 1373683.3776 | 145272.4683 | 0 | 0 | 0 | 67525.8049 | 0 | 0 | 0 | 0 | 3485789.7097 | 0 | 0 | 0 | 0 | 3485789.7097 | 20.5% | 33.27% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 3485789.7097 | 0 | 0 | 0 | 0 | 3485789.7097 | 20.5% | 33.27%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
Carbon Emissions Intensity (kg CO2e/ft²)
LEED Baseline | 265425 | 4.959 | 0 | 0 | 0 | 2.2522 | 0 | 1.3247 | 0 | 3.6418 | 0 | 0 | 0 | 1.9892 | 2.0068 | 0.14757 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.959 | 2.2522 | 1.3247 | 0 | 3.6418 | 0 | 1.9892 | 2.0068 | 0.14757 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 16.5202 | 0 | 0 | 0 | 0 | 16.5202 | [10 empty] | 16.5202 | 0 | 0 | 0 | 0 | 16.5202
Compliance Baseline | 265425 | 5.3513 | 0 | 0 | 0 | 2.9841 | 0 | 1.2769 | 0 | 3.6418 | 0 | 0 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3513 | 2.9841 | 1.2769 | 0 | 3.6418 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 19.6796 | 0 | 0 | 0 | 0 | 19.6796 | [10 empty] | 19.6796 | 0 | 0 | 0 | 0 | 19.6796
| 265425 | 5.3513 | 0 | 0 | 0 | 2.9841 | 0 | 1.2769 | 0 | 3.6418 | 0 | 0 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3513 | 2.9841 | 1.2769 | 0 | 3.6418 | 0 | 3.908 | 2.1479 | 0.17055 | 0 | 0 | 0.19906 | 0 | 0 | 0 | 0 | 19.6796 | 0 | 0 | 0 | 0 | 19.6796 | [10 empty] | 19.6796 | 0 | 0 | 0 | 0 | 19.6796
Proposed Design | 265425 | 0.71727 | 0 | 0 | 0 | 1.8884 | 0 | 0.90262 | 0 | 3.6474 | 0 | 0 | 0 | 5.1754 | 0.54732 | 0 | 0 | 0 | 0.25441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71727 | 1.8884 | 0.90262 | 0 | 3.6474 | 0 | 5.1754 | 0.54732 | 0 | 0 | 0 | 0.25441 | 0 | 0 | 0 | 0 | 13.1329 | 0 | 0 | 0 | 0 | 13.1329 | 20.5% | 33.27% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 13.1329 | 0 | 0 | 0 | 0 | 13.1329 | 20.5% | 33.27%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
Energy Cost ($)
LEED Baseline |  | 410441.1015 | 0 | 0 | 0 | 186405.7454 | 0 | 109637.9398 | 0 | 301419.3439 | 0 | 0 | 0 | 164637.5149 | 166092.9798 | 12214.2189 | 0 | 0 | 16475.4377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410441.1015 | 186405.7454 | 109637.9398 | 0 | 301419.3439 | 0 | 164637.5149 | 166092.9798 | 12214.2189 | 0 | 0 | 16475.4377 | 0 | 0 | 0 | 0 | 1367324.2818 | 0 | 0 | 0 | 0 | 1367324.2818 | [10 empty] | 1367324.2818 | 0 | 0 | 0 | 0 | 1367324.2818
Compliance Baseline |  | 442907.5302 | 0 | 0 | 0 | 246982.8319 | 0 | 105685.8746 | 0 | 301419.3439 | 0 | 0 | 0 | 323453.1702 | 177779.1943 | 14115.8848 | 0 | 0 | 16475.4377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 442907.5302 | 246982.8319 | 105685.8746 | 0 | 301419.3439 | 0 | 323453.1702 | 177779.1943 | 14115.8848 | 0 | 0 | 16475.4377 | 0 | 0 | 0 | 0 | 1628819.2674 | 0 | 0 | 0 | 0 | 1628819.2674 | [10 empty] | 1628819.2674 | 0 | 0 | 0 | 0 | 1628819.2674
|  | 163875.7862 | 0 | 0 | 0 | 91383.6478 | 0 | 39103.7736 | 0 | 301419.3439 | 0 | 0 | 0 | 119677.673 | 65778.3019 | 5222.8774 | 0 | 0 | 6095.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163875.7862 | 91383.6478 | 39103.7736 | 0 | 301419.3439 | 0 | 119677.673 | 65778.3019 | 5222.8774 | 0 | 0 | 6095.9119 | 0 | 0 | 0 | 0 | 792557.3156 | 0 | 0 | 0 | 0 | 792557.3156 | [10 empty] | 792557.3156 | 0 | 0 | 0 | 0 | 792557.3156
Proposed Design |  | 59365.9697 | 0 | 0 | 0 | 156297.8072 | 0 | 74706.7823 | 0 | 301886.7925 | 0 | 0 | 0 | 428352.8812 | 45300.017 | 0 | 0 | 0 | 21056.4338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59365.9697 | 156297.8072 | 74706.7823 | 0 | 301886.7925 | 0 | 428352.8812 | 45300.017 | 0 | 0 | 0 | 21056.4338 | 0 | 0 | 0 | 0 | 1086966.6837 | 0 | 0 | 0 | 0 | 1086966.6837 | 20.5% | 33.27% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1086966.6837 | 0 | 0 | 0 | 0 | 1086966.6837 | 20.5% | 33.27%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
Energy Cost Intensity ($/ft²)
LEED Baseline | 265425 | 1.5464 | 0 | 0 | 0 | 0.70229 | 0 | 0.41307 | 0 | 1.1356 | 0 | 0 | 0 | 0.62028 | 0.62576 | 0.046018 | 0 | 0 | 0.062072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5464 | 0.70229 | 0.41307 | 0 | 1.1356 | 0 | 0.62028 | 0.62576 | 0.046018 | 0 | 0 | 0.062072 | 0 | 0 | 0 | 0 | 5.1515 | 0 | 0 | 0 | 0 | 5.1515 | [10 empty] | 5.1515 | 0 | 0 | 0 | 0 | 5.1515
Compliance Baseline | 265425 | 1.6687 | 0 | 0 | 0 | 0.93052 | 0 | 0.39818 | 0 | 1.1356 | 0 | 0 | 0 | 1.2186 | 0.66979 | 0.053182 | 0 | 0 | 0.062072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6687 | 0.93052 | 0.39818 | 0 | 1.1356 | 0 | 1.2186 | 0.66979 | 0.053182 | 0 | 0 | 0.062072 | 0 | 0 | 0 | 0 | 6.1366 | 0 | 0 | 0 | 0 | 6.1366 | [10 empty] | 6.1366 | 0 | 0 | 0 | 0 | 6.1366
| 265425 | 0.61741 | 0 | 0 | 0 | 0.34429 | 0 | 0.14733 | 0 | 1.1356 | 0 | 0 | 0 | 0.45089 | 0.24782 | 0.019677 | 0 | 0 | 0.022967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61741 | 0.34429 | 0.14733 | 0 | 1.1356 | 0 | 0.45089 | 0.24782 | 0.019677 | 0 | 0 | 0.022967 | 0 | 0 | 0 | 0 | 2.986 | 0 | 0 | 0 | 0 | 2.986 | [10 empty] | 2.986 | 0 | 0 | 0 | 0 | 2.986
Proposed Design | 265425 | 0.22366 | 0 | 0 | 0 | 0.58886 | 0 | 0.28146 | 0 | 1.1374 | 0 | 0 | 0 | 1.6138 | 0.17067 | 0 | 0 | 0 | 0.079331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22366 | 0.58886 | 0.28146 | 0 | 1.1374 | 0 | 1.6138 | 0.17067 | 0 | 0 | 0 | 0.079331 | 0 | 0 | 0 | 0 | 4.0952 | 0 | 0 | 0 | 0 | 4.0952 | 20.5% | 33.27% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 4.0952 | 0 | 0 | 0 | 0 | 4.0952 | 20.5% | 33.27%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
| 265425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100%
EApc95 LEED Pilot ACP - Energy Performance Metric
LEED Baseline
Compliance Baseline
Proposed Design | [48 empty] | 20.5% | [15 empty] | 20.5%
[49 empty] | 100% | [15 empty] | 100%
[49 empty] | 100% | [15 empty] | 100%
[49 empty] | 100% | [15 empty] | 100%
[49 empty] | 100% | [15 empty] | 100%
[49 empty] | 100% | [15 empty] | 100%
[49 empty] | 100% | [15 empty] | 100%
[49 empty] | 100% | [15 empty] | 100%
[49 empty] | 100% | [15 empty] | 100%
[49 empty] | 100% | [15 empty] | 100%

## LEED Calc
LEED Matrix
| Basis of Energy Credit | None | LEED v2009 | LEED v4 | LEED v4 Energy Update | LEED v4.1 | LEED v5 (registered before 1/1/2028) | LEED v5 (registered after 1/1/2028)
| Site Energy | No | No | No | No | No | No | No
| Source Energy | No | No | No | Yes | No | Yes | Yes
| Carbon Emissions | No | No | No | Yes | Yes | No | No
| Costs | No | Yes | Yes | Yes | Yes | No | No
|  | None | LEED v2009 | LEED v4 | LEED v4 Energy Update | LEED v4.1 | LEED v5 (registered before 1/1/2028) | LEED v5 (registered after 1/1/2028)
| Credit 1 |  | Optimize Energy Performance | Optimize Energy Performance | Optimize Energy Performance (Cost) | Optimize Energy Performance (Cost) | Enhanced Energy Efficiency | Enhanced Energy Efficiency
| Credit 2 |  |  | EApc95 Alternative Metric | Optimize Energy Performance (Carbon) | Optimize Energy Performance (Carbon) | (with Renewables) | (with Renewables)
| Credit 3 |  | On-Site Renewable Energy | Renewable Energy Production | Renewable Energy Production | Renewable Energy | Renewable Energy | Renewable Energy
| Credit 4 | [5 empty] | Electrification | Electrification
| Credit 5 | [5 empty] | Reduced Peak Thermal Loads | Reduced Peak Thermal Loads
| Credit 1 Savings |  | 20.5% | 20.5% | 20.5% | 20.5% | 0% | 0%
| Credit 2 Savings |  |  | 20.5% | 20.5% | 20.5% | 20.5% | 20.5%
| Credit 3 Savings |  | 0% | 0% | 0% | 0% | 0% | 0%
| Credit 4 Savings | [5 empty] | 100% | 100%
Credit 5 Savings
| Credit 1 Points |  | 5 | 8 | 1 | 4 | 0 | 1
| Credit 2 Points |  |  | 8 | 1 | 3 | 2 | 2
| Credit 3 Points |  | 0 | 0 | 0 | 0 | 0 | 0
Credit 4 Points
Credit 5 Points
| Credit 1 Thresholds |  | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | 12% | 6% | 20% | 5% | 3% | 0%
|  |  | 14% | 8% | 25% | 10% | 9% | 3%
|  |  | 16% | 10% | 30% | 15% | 12% | 9%
|  |  | 18% | 12% | 35% | 20% | 15% | 12%
|  |  | 20% | 14% | 40% | 25% | 18% | 15%
|  |  | 22% | 16% | 45% | 30% | 21% | 18%
|  |  | 24% | 18% | 50% | 35% | 24% | 21%
|  |  | 26% | 20% | 55% | 40% | 27% | 24%
|  |  | 28% | 22% | 60% | 45% | 30% | 27%
|  |  | 30% | 24% | 100% | 50% | 50% | 30%
|  |  | 32% | 26% | 0% | 0% | 0% | 50%
|  |  | 34% | 29% | 0% | 0% | 0% | 0%
|  |  | 36% | 32% | 0% | 0% | 0% | 0%
|  |  | 38% | 35% | 0% | 0% | 0% | 0%
|  |  | 40% | 38% | 0% | 0% | 0% | 0%
|  |  | 42% | 42% | 0% | 0% | 0% | 0%
|  |  | 44% | 46% | 0% | 0% | 0% | 0%
|  |  | 46% | 50% | 0% | 0% | 0% | 0%
|  |  | 48% | 0% | 0% | 0% | 0% | 0%
| Credit 1 Points |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1 | 1 | 1 | 1 | 1 | 1
|  |  | 2 | 2 | 2 | 2 | 2 | 2
|  |  | 3 | 3 | 3 | 3 | 3 | 3
|  |  | 4 | 4 | 4 | 4 | 4 | 4
|  |  | 5 | 5 | 5 | 5 | 5 | 5
|  |  | 6 | 6 | 6 | 6 | 6 | 6
|  |  | 7 | 7 | 7 | 7 | 7 | 7
|  |  | 8 | 8 | 8 | 7 | 8 | 8
|  |  | 9 | 9 | 8 + EP | 8 | 9 | 9
|  |  | 10 | 10 | 0 | 8 + EP | 10 | 10
|  |  | 11 | 11 | 0 | 8 + EP | 0 | 0
|  |  | 12 | 12 | 0 | 0 | 0 | 0
|  |  | 13 | 13 | 0 | 0 | 0 | 0
|  |  | 14 | 14 | 0 | 0 | 0 | 0
|  |  | 15 | 15 | 0 | 0 | 0 | 0
|  |  | 16 | 16 | 0 | 0 | 0 | 0
|  |  | 17 | 16 | 0 | 0 | 0 | 0
|  |  | 18 | 16 | 0 | 0 | 0 | 0
|  |  | 19 | 0 | 0 | 0 | 0 | 0
| Credit 2 Thresholds |  |  | 0% | 0% | 0% | 0% | 0%
|  |  |  | 6% | 20% | 5% | 10% | 10%
|  |  |  | 8% | 25% | 10% | 20% | 20%
|  |  |  | 10% | 30% | 16% | 30% | 30%
|  |  |  | 12% | 35% | 24% | 40% | 40%
|  |  |  | 14% | 42% | 32% | 50% | 50%
|  |  |  | 16% | 50% | 40% | 60% | 60%
|  |  |  | 18% | 60% | 50% | 70% | 70%
|  |  |  | 20% | 70% | 65% | 80% | 80%
|  |  |  | 22% | 85% | 80% | 90% | 90%
|  |  |  | 24% | 100% | 100% | 100% | 100%
|  |  |  | 26% | 0% | 0% | 0% | 0%
|  |  |  | 29% | 0% | 0% | 0% | 0%
|  |  |  | 32% | 0% | 0% | 0% | 0%
|  |  |  | 35% | 0% | 0% | 0% | 0%
|  |  |  | 38% | 0% | 0% | 0% | 0%
|  |  |  | 42% | 0% | 0% | 0% | 0%
|  |  |  | 46% | 0% | 0% | 0% | 0%
|  |  |  | 50% | 0% | 0% | 0% | 0%
|  |  |  | 0% | 0% | 0% | 0% | 0%
| Credit 2 Points |  |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 1 | 1 | 1 | 1 | 1
|  |  |  | 2 | 2 | 2 | 2 | 2
|  |  |  | 3 | 3 | 3 | 3 | 3
|  |  |  | 4 | 4 | 4 | 4 | 4
|  |  |  | 5 | 5 | 5 | 5 | 5
|  |  |  | 6 | 6 | 6 | 6 | 6
|  |  |  | 7 | 7 | 7 | 7 | 7
|  |  |  | 8 | 8 | 7 | 8 | 8
|  |  |  | 9 | 8 + EP | 8 | 9 | 9
|  |  |  | 10 | 0 | 8+ EP | 10 | 10
|  |  |  | 11 | 0 | 8+ EP | 0 | 0
|  |  |  | 12 | 0 | 0 | 0 | 0
|  |  |  | 13 | 0 | 0 | 0 | 0
|  |  |  | 14 | 0 | 0 | 0 | 0
|  |  |  | 15 | 0 | 0 | 0 | 0
|  |  |  | 16 | 0 | 0 | 0 | 0
|  |  |  | 16 | 0 | 0 | 0 | 0
|  |  |  | 16 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0
| Credit 3 Thresholds |  | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | 1% | 1% | 1% | 2% | 5% | 0%
|  |  | 3% | 5% | 5% | 5% | 10% | 0%
|  |  | 5% | 10% | 10% | 10% | 20% | 0%
|  |  | 7% | 15% | 15% | 15% | 35% | 0%
|  |  | 9% | 100% | 100% | 20% | 100% | 0%
|  |  | 11% | 0% | 0% | 25% | 0% | 0%
|  |  | 13% | 0% | 0% | 100% | 0% | 0%
|  |  | 15% | 0% | 0% | 0% | 0% | 0%
|  |  | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | 0% | 0% | 0% | 0% | 0% | 0%
| Credit 3 Points |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1 | 1 | 1 | 1 | 1 | 0
|  |  | 2 | 2 | 2 | 2 | 2 | 0
|  |  | 3 | 3 | 3 | 3 | 3 | 0
|  |  | 4 | 3 + 1 EP | 3 + 1 EP | 4 | 4 | 0
|  |  | 5 | 3 + 1 EP | 3 + 1 EP | 5 | 5 | 0
|  |  | 6 | 0 | 0 | 5 + 1 EP | 0 | 0
|  |  | 7 | 0 | 0 | 5 + 1 EP | 0 | 0
|  |  | 7 + 1 EP | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0

## RefTable LEED
LEED Tables
| LEED Points | LEED v2009 | [5 empty] | LEED v4 | [7 empty] | LEED v4 Energy Update | [8 empty] | LEED v4.1 | [6 empty] | LEED v5 (registered before 1/1/2028) | [8 empty] | LEED v5 (registered after 1/1/2028)
|  | New Buildings | Existing Building and Renovations | NC + Schools | Core and Shell | Percentage | Points | New Construction | Major Renovation | Core and Shell | All but Healthcare + Schools | Healthcare | School | Percentage | Points | New Construction + Major Renovations | Schools | Core and Shell | Healthcare | All but Healthcare + Schools | Healthcare | School | Percentage | Points | New Construction | Healthcare, Major Renovations, Core and Shell | All but Healthcare + Schools | Healthcare | School | Percentage | Points | New Construction | Core and Shell |  |  | All |  |  | Percentage | Points | New Construction | Core and Shell | All | Percentage | Points
|  | Optimize Energy Performance | [5 empty] | Optimize Energy Performance | [7 empty] | Optimize Energy Performance (Cost) | [8 empty] | Optimize Energy Performance (Cost) | [6 empty] | Enhanced Energy Efficiency | [8 empty] | Enhanced Energy Efficiency
|  | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0 |  |  | 0% | 0 | 0% |  | 0 | 0% | 0
|  | 12% | 8% | 1 | 3 | 12% | 1 | 6% | 4% | 3% | 1 | 3 | 1 | 6% | 1 | 20% | 20% | 10% | 7% | 1 | 1 | 1 | 20% | 1 | 5% | 2% | 1 | 1 | 1 | 5% | 1 | 3% | 2% | 2% | 10% | 1 |  |  | 3% | 1 | 3% |  | 1 | 3% | 1
|  | 14% | 10% | 2 | 4 | 14% | 2 | 8% | 6% | 5% | 2 | 4 | 2 | 8% | 2 | 25% | 25% | 15% | 10% | 2 | 2 | 2 | 25% | 2 | 10% | 5% | 2 | 2 | 2 | 10% | 2 | 9% | 5% | 5% | 20% | 2 |  |  | 9% | 2 | 9% |  | 2 | 9% | 2
|  | 16% | 12% | 3 | 5 | 16% | 3 | 10% | 8% | 7% | 3 | 5 | 3 | 10% | 3 | 30% | 30% | 20% | 15% | 3 | 3 | 3 | 30% | 3 | 15% | 10% | 3 | 3 | 3 | 15% | 3 | 12% | 8% | 8% | 30% | 3 |  |  | 12% | 3 | 12% | 0% | 3 | 12% | 3
|  | 18% | 14% | 4 | 6 | 18% | 4 | 12% | 10% | 9% | 4 | 6 | 4 | 12% | 4 | 35% | 35% | 25% | 20% | 4 | 4 | 4 | 35% | 4 | 20% | 15% | 4 | 4 | 4 | 20% | 4 | 15% | 11% | 11% | 40% | 4 |  |  | 15% | 4 | 15% | 3% | 4 | 15% | 4
|  | 20% | 16% | 5 | 7 | 20% | 5 | 14% | 12% | 11% | 5 | 7 | 5 | 14% | 5 | 40% | 40% | 30% | 25% | 5 | 5 | 5 | 40% | 5 | 25% | 20% | 5 | 5 | 5 | 25% | 5 | 18% | 14% | 14% | 50% | 5 |  |  | 18% | 5 | 18% | 6% | 5 | 18% | 5
|  | 22% | 18% | 6 | 8 | 22% | 6 | 16% | 14% | 13% | 6 | 8 | 6 | 16% | 6 | 45% | 45% | 35% | 30% | 6 | 6 | 6 | 45% | 6 | 30% | 25% | 6 | 6 | 6 | 30% | 6 | 21% | 17% | 17% | 60% | 6 |  |  | 21% | 6 | 21% | 9% | 6 | 21% | 6
|  | 24% | 20% | 7 | 9 | 24% | 7 | 18% | 16% | 15% | 7 | 9 | 7 | 18% | 7 | 50% | 50% | 40% | 35% | 7 | 7 | 7 | 50% | 7 | 35% | 30% | 7 | 7 | 7 | 35% | 7 | 24% | 20% | 20% | 70% | 7 |  |  | 24% | 7 | 24% | 12% | 7 | 24% | 7
|  | 26% | 22% | 8 | 10 | 26% | 8 | 20% | 18% | 17% | 8 | 10 | 8 | 20% | 8 | 55% | 60% | 45% | 40% | 8 | 8 | 8 | 55% | 8 | 40% | 35% | 8 | 8 | 7 | 40% | 7 | 27% |  |  |  | 8 |  |  | 27% | 8 | 27% |  | 8 | 27% | 8
|  | 28% | 24% | 9 | 11 | 28% | 9 | 22% | 20% | 19% | 9 | 11 | 9 | 22% | 9 | 60% | 100% | 50% | 45% | 9 | 9 | 8 + EP | 60% | 8 + EP | 45% | 40% | 9 | 9 | 8 | 45% | 8 | 30% |  |  |  | 9 |  |  | 30% | 9 | 30% |  | 9 | 30% | 9
|  | 30% | 26% | 10 | 12 | 30% | 10 | 24% | 22% | 21% | 10 | 12 | 10 | 24% | 10 | 100% |  | 100% | 50% | 9 + EP | 10 |  | 100% | 0 | 50% | 45% | 9 + EP | 10 | 8 + EP | 50% | 8 + EP | 50% |  |  |  | 10 |  |  | 50% | 10 | 50% |  | 10 | 50% | 10
|  | 32% | 28% | 11 | 13 | 32% | 11 | 26% | 24% | 23% | 11 | 13 | 11 | 26% | 11 |  |  |  | 100% |  | 10 + EP |  | 0% | 0 |  | 50% | 9 + EP | 10 | 8 + EP | 0% | 8 + EP | [7 empty] | 0% | 0 |  |  |  | 0% | 0
|  | 34% | 30% | 12 | 14 | 34% | 12 | 29% | 27% | 26% | 12 | 14 | 12 | 29% | 12 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
|  | 36% | 32% | 13 | 15 | 36% | 13 | 32% | 30% | 29% | 13 | 15 | 13 | 32% | 13 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
|  | 38% | 34% | 14 | 16 | 38% | 14 | 35% | 33% | 32% | 14 | 16 | 14 | 35% | 14 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
|  | 40% | 36% | 15 | 17 | 40% | 15 | 38% | 36% | 35% | 15 | 17 | 15 | 38% | 15 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
|  | 42% | 38% | 16 | 18 | 42% | 16 | 42% | 40% | 39% | 16 | 18 | 16 | 42% | 16 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
|  | 44% | 40% | 17 | 19 | 44% | 17 | 46% | 44% | 43% | 17 | 19 | 16 | 46% | 16 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
|  | 46% | 42% | 18 | 20 | 46% | 18 | 50% | 48% | 47% | 18 | 20 | 16 | 50% | 16 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
|  | 48% | 44% | 19 | 21 | 48% | 19 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
[8 empty] | EApc95 Alternative Metric | [7 empty] | Optimize Energy Performance (Carbon) | [8 empty] | Optimize Energy Performance (Carbon) | [6 empty] | (with Renewables)
[8 empty] | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0 | 0% | 0% |  |  | 0 |  |  | 0% | 0 | 0% |  | 0 | 0% | 0
[8 empty] | 6% | 4% | 3% | 1 | 3 | 1 | 6% | 1 | 20% | 20% | 10% | 7% | 1 | 1 | 1 | 20% | 1 | 5% | 2% | 1 | 1 | 1 | 5% | 1 | 10% | 10% |  |  | 1 |  |  | 10% | 1 | 10% |  | 1 | 10% | 1
[8 empty] | 8% | 6% | 5% | 2 | 4 | 2 | 8% | 2 | 25% | 25% | 15% | 10% | 2 | 2 | 2 | 25% | 2 | 10% | 5% | 2 | 2 | 2 | 10% | 2 | 20% | 20% |  |  | 2 |  |  | 20% | 2 | 20% | 0% | 2 | 20% | 2
[8 empty] | 10% | 8% | 7% | 3 | 5 | 3 | 10% | 3 | 30% | 30% | 20% | 15% | 3 | 3 | 3 | 30% | 3 | 16% | 10% | 3 | 3 | 3 | 16% | 3 | 30% | 30% |  |  | 3 |  |  | 30% | 3 | 30% | 13% | 3 | 30% | 3
[8 empty] | 12% | 10% | 9% | 4 | 6 | 4 | 12% | 4 | 35% | 35% | 25% | 21% | 4 | 4 | 4 | 35% | 4 | 24% | 16% | 4 | 4 | 4 | 24% | 4 | 40% | 40% |  |  | 4 |  |  | 40% | 4 | 40% | 26% | 4 | 40% | 4
[8 empty] | 14% | 12% | 11% | 5 | 7 | 5 | 14% | 5 | 42% | 42% | 32% | 27% | 5 | 5 | 5 | 42% | 5 | 32% | 24% | 5 | 5 | 5 | 32% | 5 | 50% | 50% |  |  | 5 |  |  | 50% | 5 | 50% | 39% | 5 | 50% | 5
[8 empty] | 16% | 14% | 13% | 6 | 8 | 6 | 16% | 6 | 50% | 50% | 40% | 35% | 6 | 6 | 6 | 50% | 6 | 40% | 32% | 6 | 6 | 6 | 40% | 6 | 60% | 60% |  |  | 6 |  |  | 60% | 6 | 60% | 52% | 6 | 60% | 6
[8 empty] | 18% | 16% | 15% | 7 | 9 | 7 | 18% | 7 | 60% | 60% | 50% | 45% | 7 | 7 | 7 | 60% | 7 | 50% | 40% | 7 | 7 | 7 | 50% | 7 | 70% | 70% |  |  | 7 |  |  | 70% | 7 | 70% | 65% | 7 | 70% | 7
[8 empty] | 20% | 18% | 17% | 8 | 10 | 8 | 20% | 8 | 70% | 70% | 60% | 55% | 8 | 8 | 8 | 70% | 8 | 65% | 50% | 8 | 8 | 7 | 65% | 7 | 80% |  |  |  | 8 |  |  | 80% | 8 | 80% |  | 8 | 80% | 8
[8 empty] | 22% | 20% | 19% | 9 | 11 | 9 | 22% | 9 | 85% | 100% | 75% | 65% | 9 | 9 | 8 + EP | 85% | 8 + EP | 80% | 65% | 9 | 9 | 8 | 80% | 8 | 90% |  |  |  | 9 |  |  | 90% | 9 | 90% |  | 9 | 90% | 9
[8 empty] | 24% | 22% | 21% | 10 | 12 | 10 | 24% | 10 | 100% |  | 100% | 80% | 9 + EP | 10 |  | 100% | 0 | 100% | 80% | 9+ EP | 10 | 8+ EP | 100% | 8+ EP | 100% |  |  |  | 10 |  |  | 100% | 10 | 100% |  | 10 | 100% | 10
[8 empty] | 26% | 24% | 23% | 11 | 13 | 11 | 26% | 11 |  |  |  | 100% |  | 10 + EP |  | 0% | 0 |  | 100% |  | 10+ EP | 8+ EP | 0% | 8+ EP |  |  |  |  | 0 |  |  | 0% | 0 |  |  | 0 | 0% | 0
[8 empty] | 29% | 27% | 26% | 12 | 14 | 12 | 29% | 12 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 |  |  |  |  | 0 |  |  | 0% | 0 |  |  | 0 | 0% | 0
[8 empty] | 32% | 30% | 29% | 13 | 15 | 13 | 32% | 13 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 |  |  |  |  | 0 |  |  | 0% | 0 |  |  | 0 | 0% | 0
[8 empty] | 35% | 33% | 32% | 14 | 16 | 14 | 35% | 14 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 |  |  |  |  | 0 |  |  | 0% | 0 |  |  | 0 | 0% | 0
[8 empty] | 38% | 36% | 35% | 15 | 17 | 15 | 38% | 15 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 |  |  |  |  | 0 |  |  | 0% | 0 |  |  | 0 | 0% | 0
[8 empty] | 42% | 40% | 39% | 16 | 18 | 16 | 42% | 16 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 |  |  |  |  | 0 |  |  | 0% | 0 |  |  | 0 | 0% | 0
[8 empty] | 46% | 44% | 43% | 17 | 19 | 16 | 46% | 16 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 |  |  |  |  | 0 |  |  | 0% | 0 |  |  | 0 | 0% | 0
[8 empty] | 50% | 48% | 47% | 18 | 20 | 16 | 50% | 16 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 |  |  |  |  | 0 |  |  | 0% | 0 |  |  | 0 | 0% | 0
[14 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 |  |  |  |  | 0 |  |  | 0% | 0 |  |  | 0 | 0% | 0
|  | On-Site Renewable Energy | [5 empty] | Renewable Energy Production | [7 empty] | Renewable Energy Production | [8 empty] | Renewable Energy | [6 empty] | Renewable Energy | [8 empty] | Renewable Energy
|  | 0% | 0% | 0 | 0 | 0% | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0% | 0 | 0% |  | 0% |  | 0 | 0 | 0 | 0% | 0 |  |  |  | 0% | 0
|  | 1% | 1% | 1 | 1 | 1% | 1 | 1% | 1% | 1% | 1 | 1 | 1 | 1% | 1 | 1% | 1% | 1% | 1% | 1 | 1 | 1 | 1% | 1 | 2% | 2% | 1 | 1 | 1 | 2% | 1 | 5% |  | 15% |  | 1 | 1 | 1 | 5% | 1 |  |  |  | 0% | 0
|  | 3% | 3% | 2 |  | 3% | 2 | 5% | 5% | 3% | 2 | 2 | 2 | 5% | 2 | 5% | 5% | 3% | 3% | 2 | 2 | 2 | 5% | 2 | 5% | 5% | 2 | 2 | 2 | 5% | 2 | 10% |  | 30% |  | 2 | 2 | 2 | 10% | 2 |  |  |  | 0% | 0
|  | 5% | 5% | 3 |  | 5% | 3 | 10% | 10% | 5% | 3 | 3 | 3 | 10% | 3 | 10% | 10% | 5% | 5% | 3 | 3 | 3 | 10% | 3 | 10% | 10% | 3 | 3 | 3 | 10% | 3 | 20% |  | 65% |  | 3 | 3 | 3 | 20% | 3 |  |  |  | 0% | 0
|  | 7% | 7% | 4 |  | 7% | 4 | 15% | 15% | 10% | 3 + 1 EP | 3 + 1 EP | 3 + 1 EP | 15% | 3 + 1 EP | 15% | 15% | 10% | 10% | 3 + 1 EP | 3 + 1 EP | 3 + 1 EP | 15% | 3 + 1 EP | 15% | 15% | 4 | 4 | 4 | 15% | 4 | 35% |  |  |  | 4 | 4 | 4 | 35% | 4 |  |  |  | 0% | 0
|  | 9% | 9% | 5 |  | 9% | 5 | 100% | 100% | 100% | 3 + 1 EP | 3 + 1 EP | 3 + 1 EP | 100% | 3 + 1 EP | 100% | 100% | 100% | 100% | 3 + 1 EP | 3 + 1 EP | 3 + 1 EP | 100% | 3 + 1 EP | 20% | 20% | 5 | 5 | 5 | 20% | 5 | 100% |  |  |  | 5 | 5 | 5 | 100% | 5 |  |  |  | 0% | 0
|  | 11% | 11% | 6 |  | 11% | 6 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | 25% | 25% | 5 + 1 EP | 5 + 1 EP | 5 + 1 EP | 25% | 5 + 1 EP | [5 empty] | 5 + 1 EP | 5 + 1 EP | 0% | 0 |  |  |  | 0% | 0
|  | 13% | 13% | 7 |  | 13% | 7 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | 100% | 100% | 5 + 1 EP | 5 + 1 EP | 5 + 1 EP | 100% | 5 + 1 EP | [5 empty] | 5 + 1 EP | 5 + 1 EP | 0% | 0 |  |  |  | 0% | 0
|  | 15% | 15% | 7 + 1 EP |  | 15% | 7 + 1 EP | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
[6 empty] | 0% | 0 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
[6 empty] | 0% | 0 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
[6 empty] | 0% | 0 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
[6 empty] | 0% | 0 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
[6 empty] | 0% | 0 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
[6 empty] | 0% | 0 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
[6 empty] | 0% | 0 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
[6 empty] | 0% | 0 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
[6 empty] | 0% | 0 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
[6 empty] | 0% | 0 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0
[6 empty] | 0% | 0 | [6 empty] | 0% | 0 | [7 empty] | 0% | 0 | [5 empty] | 0% | 0 | [7 empty] | 0% | 0 |  |  |  | 0% | 0

## RefTable BPF
Building Performance Factor Lookup Tables
| Building Performance Factors | ASHRAE 2019/IECC 2021 | [18 empty] | Boston Stretch Code | Factors Used
| Building Type | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 | 5A
| Multifamily | 0.68 | 0.7 | 0.68 | 0.7 | 0.66 | 0.66 | 0.69 | 0.68 | 0.59 | 0.74 | 0.76 | 0.74 | 0.7 | 0.73 | 0.75 | 0.68 | 0.71 | 0.68 | 0.72 | 0.51 | 0.74
| Healthcare/Hospital | 0.6 | 0.6 | 0.6 | 0.6 | 0.58 | 0.54 | 0.56 | 0.55 | 0.55 | 0.55 | 0.54 | 0.54 | 0.57 | 0.52 | 0.54 | 0.57 | 0.52 | 0.57 | 0.57 | 0.59 | 0.55
| Hotel/Motel | 0.55 | 0.53 | 0.55 | 0.53 | 0.53 | 0.52 | 0.53 | 0.54 | 0.54 | 0.53 | 0.53 | 0.52 | 0.5 | 0.51 | 0.51 | 0.5 | 0.51 | 0.5 | 0.5 | 0.57 | 0.53
| Office | 0.52 | 0.57 | 0.52 | 0.57 | 0.5 | 0.56 | 0.53 | 0.56 | 0.48 | 0.51 | 0.52 | 0.49 | 0.51 | 0.51 | 0.49 | 0.52 | 0.51 | 0.49 | 0.51 | 0.51 | 0.51
| Restaurant | 0.63 | 0.64 | 0.63 | 0.64 | 0.6 | 0.6 | 0.6 | 0.61 | 0.58 | 0.62 | 0.57 | 0.61 | 0.63 | 0.6 | 0.64 | 0.65 | 0.62 | 0.67 | 0.7 | 0.62 | 0.62
| Retail | 0.51 | 0.54 | 0.51 | 0.54 | 0.49 | 0.55 | 0.51 | 0.55 | 0.53 | 0.51 | 0.55 | 0.54 | 0.5 | 0.54 | 0.55 | 0.5 | 0.51 | 0.48 | 0.5 | 0.47 | 0.51
| School | 0.39 | 0.47 | 0.39 | 0.47 | 0.38 | 0.43 | 0.38 | 0.42 | 0.4 | 0.37 | 0.4 | 0.38 | 0.36 | 0.4 | 0.36 | 0.36 | 0.37 | 0.36 | 0.37 | 0.51 | 0.37
| Warehouse | 0.38 | 0.42 | 0.38 | 0.42 | 0.4 | 0.42 | 0.43 | 0.44 | 0.43 | 0.44 | 0.43 | 0.46 | 0.49 | 0.47 | 0.48 | 0.54 | 0.51 | 0.57 | 0.57 | 0.41 | 0.44
| All Others | 0.56 | 0.57 | 0.56 | 0.57 | 0.5 | 0.52 | 0.5 | 0.54 | 0.53 | 0.53 | 0.52 | 0.54 | 0.51 | 0.51 | 0.5 | 0.5 | 0.5 | 0.5 | 0.46 | 0.51 | 0.53
| Building Performance Factors | LEED v5 (registered before 1/1/2028)
| Building Type | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| Multifamily | 0.74 | 0.69 | 0.73 | 0.7 | 0.73 | 0.7 | 0.71 | 0.7 | 0.63 | 0.7 | 0.71 | 0.69 | 0.68 | 0.7 | 0.7 | 0.68 | 0.68 | 0.68 | 0.74
| Healthcare/Hospital | 0.72 | 0.72 | 0.73 | 0.73 | 0.74 | 0.71 | 0.72 | 0.74 | 0.71 | 0.72 | 0.73 | 0.71 | 0.74 | 0.73 | 0.8 | 0.73 | 0.77 | 0.78 | 0.79
| Hotel/Motel | 0.72 | 0.71 | 0.72 | 0.71 | 0.71 | 0.7 | 0.71 | 0.73 | 0.72 | 0.71 | 0.73 | 0.73 | 0.71 | 0.73 | 0.74 | 0.7 | 0.72 | 0.7 | 0.7
| Office | 0.62 | 0.63 | 0.61 | 0.62 | 0.58 | 0.6 | 0.57 | 0.62 | 0.55 | 0.55 | 0.61 | 0.57 | 0.58 | 0.61 | 0.59 | 0.58 | 0.6 | 0.54 | 0.58
| Restaurant | 0.65 | 0.62 | 0.63 | 0.61 | 0.62 | 0.58 | 0.63 | 0.63 | 0.63 | 0.67 | 0.66 | 0.66 | 0.7 | 0.7 | 0.68 | 0.73 | 0.72 | 0.74 | 0.77
| Retail | 0.57 | 0.54 | 0.53 | 0.53 | 0.48 | 0.47 | 0.47 | 0.47 | 0.47 | 0.52 | 0.5 | 0.56 | 0.57 | 0.53 | 0.59 | 0.58 | 0.56 | 0.53 | 0.6
| School | 0.57 | 0.57 | 0.58 | 0.57 | 0.55 | 0.54 | 0.57 | 0.51 | 0.49 | 0.48 | 0.51 | 0.52 | 0.51 | 0.53 | 0.51 | 0.53 | 0.5 | 0.51 | 0.58
| Warehouse | 0.28 | 0.3 | 0.24 | 0.27 | 0.23 | 0.24 | 0.27 | 0.23 | 0.2 | 0.33 | 0.26 | 0.28 | 0.4 | 0.32 | 0.29 | 0.44 | 0.38 | 0.4 | 0.44
| All Others | 0.65 | 0.62 | 0.64 | 0.62 | 0.57 | 0.54 | 0.57 | 0.56 | 0.58 | 0.59 | 0.57 | 0.6 | 0.6 | 0.59 | 0.65 | 0.62 | 0.62 | 0.61 | 0.64
| Building Performance Factors | LEED v5 (registered after 1/1/2028)
| Building Type | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| Multifamily | 0.64 | 0.59 | 0.62 | 0.6 | 0.61 | 0.59 | 0.61 | 0.6 | 0.49 | 0.57 | 0.59 | 0.56 | 0.55 | 0.57 | 0.57 | 0.55 | 0.55 | 0.55 | 0.6
| Healthcare/hospital | 0.64 | 0.64 | 0.66 | 0.65 | 0.66 | 0.63 | 0.64 | 0.65 | 0.63 | 0.64 | 0.65 | 0.62 | 0.64 | 0.62 | 0.69 | 0.63 | 0.68 | 0.69 | 0.7
| Hotel/motel | 0.65 | 0.63 | 0.64 | 0.63 | 0.62 | 0.61 | 0.62 | 0.63 | 0.62 | 0.59 | 0.6 | 0.6 | 0.57 | 0.58 | 0.59 | 0.56 | 0.58 | 0.56 | 0.56
| Office | 0.54 | 0.54 | 0.53 | 0.54 | 0.49 | 0.52 | 0.49 | 0.52 | 0.45 | 0.46 | 0.52 | 0.47 | 0.48 | 0.51 | 0.48 | 0.48 | 0.5 | 0.45 | 0.49
| Restaurant | 0.61 | 0.58 | 0.58 | 0.57 | 0.57 | 0.54 | 0.58 | 0.59 | 0.57 | 0.62 | 0.61 | 0.61 | 0.65 | 0.64 | 0.63 | 0.67 | 0.66 | 0.69 | 0.72
| Retail | 0.47 | 0.45 | 0.44 | 0.44 | 0.4 | 0.39 | 0.37 | 0.39 | 0.36 | 0.4 | 0.41 | 0.42 | 0.45 | 0.43 | 0.46 | 0.44 | 0.43 | 0.42 | 0.46
| School | 0.52 | 0.53 | 0.53 | 0.53 | 0.51 | 0.51 | 0.53 | 0.48 | 0.46 | 0.43 | 0.48 | 0.47 | 0.45 | 0.49 | 0.46 | 0.46 | 0.44 | 0.44 | 0.48
| Warehouse | 0.25 | 0.25 | 0.21 | 0.24 | 0.2 | 0.21 | 0.24 | 0.2 | 0.17 | 0.3 | 0.22 | 0.25 | 0.36 | 0.28 | 0.25 | 0.4 | 0.34 | 0.36 | 0.4
| All others | 0.58 | 0.56 | 0.56 | 0.56 | 0.5 | 0.47 | 0.49 | 0.48 | 0.48 | 0.49 | 0.49 | 0.5 | 0.51 | 0.5 | 0.55 | 0.52 | 0.52 | 0.52 | 0.55

## Conversions
Conversion Factors
Energy Conversion Table
| To/From | kWh | MWh | GJ | kBtu | MBtu | 1000 ft3 Gas | Therm | Conversions and Constants | Value | Description
| kWh | 1 | 1000 | 277.7778 | 0.29307 | 293.0712 | 293.0832 | 29.2997 | l/s to kg/s | 0.00121 | 1000 L/m^3, 1.21 kg/m^3 air
| MWh | 0.001 | 1 | 0.27778 | 0.0034121 | 3.4121e-06 | 0.29308 | 0.0293 | kg/s to l/s | 826.4463 | 1/(l/s to kg/s) air
| GJ | 0.0036 | 3.6 | 1 | 0.012284 | 1.2284e-05 | 1.0551 | 0.10551
| kBtu | 3.4121 | 3412.14 | 948 | 1 | 1000 | 1038 | 100 | sq ft to sq m | 0.092903 | (12 in/ft, 0.0254 m/in)^2
| MBtu | 0.0034121 | 3.4121 | 0.948 | 0.001 | 1 | 1.038 | 0.1 | sq m to sq ft | 10.7639 | 1/(sq ft to sq m)
| 1000 ft3 Gas | 0.003412 | 3.412 | 0.948 | 0.011642 | 1.1642e-05 | 1 | 0.1 | Density of air | 1.21 | kg/m^3
| Therm | 0.03413 | 34.1296 | 9.4804 | 0.01 | 1e-05 | 10.38 | 1 | kg/s to m^3/s | 0.82645 | kgps_m3ps (air only)
[9 empty] | CFM to m^3/s | 0.00047195 | (12in/ft*0.0254in/m)^3*1min/60s)
| Energy Use Intensity Conversion Table | [7 empty] | m^3/s to CFM | 2118.88 | (CFM_to_m3ps)^-1
[9 empty] | inH2O_kPa | 0.24908 | Unitconversion.org: 1 kPa = 4.014742133 in H2O (4°C inAq)
| To/From | kWh/m² | kwh/ft² | kBtu/ft² |  |  |  |  | kPa_inH2O | 4.0147
| kWh/m² | 1 | 10.7639 | 3.1546 |  |  |  |  | W to Btu/h | 3.4121 | Unitconversion.org: 1 watt = 3.412141633 Btu
| kwh/ft² | 0.092903 | 1 | 0.29307 |  |  |  |  | Btu/h to W | 0.29307
| kBtu/ft² | 0.317 | 3.4121 | 1 |  |  |  |  | ton to Btu/h | 12000 | 1 ton = 12,000 Btu/hr
[9 empty] | Btu/h to ton | 8.3333e-05
| Carbon Emissions Conversion Table | [7 empty] | kW to ton | 0.28433 | 1 ton = 3.517 kW
[9 empty] | ton to kW | 3.517
| To/From | kg CO2e | lbs CO2e | MT CO2e |  |  |  |  | g/kg to grains/lbm H20 | 7 | 7 grains/lbm per 1 g/kg H20
| kg CO2e | 1 | 0.45359 | 1000 |  |  |  |  | gr./lbm to g/kg | 0.14286
| lbs CO2e | 2.2046 | 1 | 2204.62 |  |  |  |  | Therm to kWh | 29.3072 | 1 Therm = 29.30722 kWh
| MT CO2e | 0.001 | 0.00045359 | 1 |  |  |  |  | kWh to Therm | 0.034121
[9 empty] | w to kW | 0.001 | 0.001 kW per W
| Area Conversion Table | [7 empty] | kW_w | 1000 | 1000 W per kW
[9 empty] | hours to minutes | 60 | 60 minutes/hour
| To/From | ft² | m² | [5 empty] | minutes to hours | 0.016667
| ft² | 1 | 0.092903 | [5 empty] | seconds_hours | 0.00027778 | 3600 s / 1 hour
| m² | 10.7639 | 1 | [5 empty] | si_cp_h20 | 4.186 | 4.186 kJ/kg
[9 empty] | si density of h20 | 1000 | 1000 kg water / m3
[9 empty] | kJ to ton-hr | 7.8985e-05 | Unitconversion.org 12660.67023144 kJ = 1 ton-hr
[9 empty] | ton-hr to kJ | 12660.6702