## Data Mapping
Category | Field | Source Report | Section / Column | Derivation Method | Proposed Value | Baseline Value | Notes / Formula
Project Info | Option Name | LEED Summary | Section 1.1 General Information | Direct read | Primary | ASHRAE 90.1-2010 Baseline
Project Info | Climate File | LEED Summary | Section 1.1 — Weather File | Direct read | CZ10RV2 | CZ10RV2 WMO722860
Project Info | Climate Zone | LEED Summary | Section 1.1 — Climate Zone | Direct read | 3B | 3B
Project Info | Heating Unmet Hours | LEED Summary | Table EAp2-2 Advisory Messages | Direct read | 91 | 0
Project Info | Cooling Unmet Hours | LEED Summary | Table EAp2-2 Advisory Messages | Direct read | 346 | 1568
Energy Consumption | Total Energy Use (kBtu) | LEED Summary | Table EAp2-6 — Total kWh | Calculated | 534,633 | 689,000–696,000 (by rotation) | Total kWh × 3.412 = kBtu
Energy Consumption | Energy Use Intensity (kBtu/ft²) | Site Consumption Summary | Grand Total — Site EUI | Direct read | 25.33 | 32.84
Energy Consumption | Electricity (kBtu) | LEED Summary | Table EAp2-6 — Electricity kWh | Calculated | 534,633 | varies by rotation | Electricity kWh × 3.412 = kBtu
Energy Consumption | Gas (kBtu) | LEED Summary | Table EAp2-6 — Natural Gas | Direct read (0) | 0 | 0 | All-electric building — no gas
Energy Consumption | Heating Electricity (kBtu) | LEED Summary | Table EAp2-4/5 — Heating kWh | Calculated | 42,756 | 37,501–39,262 | Heating kWh × 3.412 = kBtu
Energy Consumption | Cooling Electricity (kBtu) | LEED Summary | Table EAp2-4/5 — Cooling kWh | Calculated | 116,164 | 140,537–145,091 | Cooling kWh × 3.412 = kBtu
Energy Consumption | Interior Lighting (kBtu) | LEED Summary | Table EAp2-4/5 — Int. Lighting kWh | Calculated | 124,771 | 153,373 | Lighting kWh × 3.412 = kBtu
Energy Consumption | Interior Equipment (kBtu) | LEED Summary | Table EAp2-4/5 — Int. Equipment kWh | Calculated | 180,085 | 180,085 | Equipment kWh × 3.412 = kBtu
Energy Consumption | Fans (kBtu) | LEED Summary | Table EAp2-4/5 — Fans kWh | Calculated | 70,867 | 170,143–177,124 | Fan kWh × 3.412 = kBtu
Energy Consumption | All other end uses | All reports | No district energy, no pumps | Direct read (0) | 0 | 0
Economics & Carbon | Total Energy Cost ($) | LEED Summary | Table EAp2-7 — Total Energy Cost | Direct read | $19,292 | $25,381
Economics & Carbon | Energy Cost Intensity ($/ft²) | LEED Summary | Table EAp2-7 ÷ conditioned area | Calculated | $1.41 | $1.86 | Total Energy Cost ($) ÷ Conditioned Floor Area (ft²)
Economics & Carbon | Electricity Virtual Rate ($/kBtu) | LEED Summary | Section 1.5 — rate $/kWh | Calculated | $0.0361/kBtu | $0.0366/kBtu | $/kWh ÷ 3.412 = $/kBtu
Economics & Carbon | Total Carbon Emissions (kg CO₂e) | Derived | Total kBtu × CA grid factor | Calculated | 28,336 kg | 36,540 kg | Total kBtu × 0.053 kg CO₂e/kBtu (CA grid factor)
Economics & Carbon | Carbon Intensity (kg CO₂e/ft²) | Derived | Total carbon ÷ conditioned area | Calculated | 2.08 | 2.68 | Total Carbon (kg) ÷ Conditioned Floor Area (ft²)
Economics & Carbon | Carbon Virtual Rate | Derived | CA grid carbon factor | Standard reference | 0.053 | 0.053 | 0.053 kg CO₂e/kBtu — California grid emission factor
Peak Loads | Peak Heating (kBtuh) | LEED Summary | Table EAp2-5 — Heating Demand kW | Calculated | 305 | 786 | Peak Heating kW × 3.412 = kBtuh
Peak Loads | Peak Cooling (kBtuh) | LEED Summary | Table EAp2-5 — Cooling Demand kW | Calculated | 300 | 360 | Peak Cooling kW × 3.412 = kBtuh
Peak Loads | Peak Electrical Load (W) | LEED Summary | Peak Demand kW | Calculated | 37,000 W | 49,000 W | Peak Demand kW × 1,000 = W
Peak Loads | Peak Heating/Cooling/Elec Hour | NOT IN REPORTS | Timestamp not exported in any TRACE CSV | ⚠ Manual Entry Required | — | — | Hour-of-peak not output in any TRACE 3D Plus CSV report — enter manually from model
Building Geometry | Conditioned Floor Area (ft²) | LEED Summary | Table EAp2-1 — Regularly Occupied Area | Direct read | 13,652 | 13,652
Building Geometry | Total Floor Area (ft²) | LEED Summary | Table EAp2-1 — Total gross floor area | Direct read | 21,103 | 21,103
Building Geometry | Gross Wall Area (ft²) | Envelope Summary | Summary — Total Gross Wall Area | Direct read | 11,729 | 11,729
Building Geometry | North Wall Area (ft²) | Envelope Summary | Above Ground Wall Area — North | Direct read | 2,721 | 2,721
Building Geometry | East Wall Area (ft²) | Envelope Summary | Above Ground Wall Area — East | Direct read | 2,651 | 2,651
Building Geometry | South Wall Area (ft²) | Envelope Summary | Above Ground Wall Area — South | Direct read | 3,382 | 3,382
Building Geometry | West Wall Area (ft²) | Envelope Summary | Above Ground Wall Area — West | Direct read | 2,975 | 2,975
Building Geometry | Gross Roof Area (ft²) | Envelope Summary | Summary — Gross Roof Area | Direct read | 15,695 | 15,695
Building Geometry | Skylight Ratio (%) | Envelope Summary | Skylight-Roof Ratio row | Direct read | 0% | 0%
Building Geometry | Wall-to-Floor Ratio | Derived | Gross Wall Area ÷ Conditioned Floor Area | Calculated | 0.859 | 0.859 | Gross Wall Area (ft²) ÷ Conditioned Floor Area (ft²)
Building Geometry | Roof-to-Floor Ratio | Derived | Gross Roof Area ÷ Conditioned Floor Area | Calculated | 1.150 | 1.150 | Gross Roof Area (ft²) ÷ Conditioned Floor Area (ft²)
WWR | Building WWR Actual (%) | Envelope Summary | Summary — Gross Window-Wall Ratio | Direct read | 7.05% | 7.05%
WWR | North WWR Nominal (%) | Envelope Summary | Above Ground Window-Wall Ratio — North | Direct read | 8.22% | 8.22%
WWR | East WWR Nominal (%) | Envelope Summary | Above Ground Window-Wall Ratio — East | Direct read | 10.45% | 10.45%
WWR | South WWR Nominal (%) | Envelope Summary | Above Ground Window-Wall Ratio — South | Direct read | 5.06% | 5.06%
WWR | West WWR Nominal (%) | Envelope Summary | Above Ground Window-Wall Ratio — West | Direct read | 5.22% | 5.22%
WWR | North WWR Actual (%) | Envelope Summary | Window Opening Area N ÷ Gross Wall Area N | Calculated | 8.23% | 8.23% | (Window Area N ÷ Wall Area N) × 100 = (224 ÷ 2,721) × 100
WWR | East WWR Actual (%) | Envelope Summary | Window Opening Area E ÷ Gross Wall Area E | Calculated | 10.45% | 10.45% | (Window Area E ÷ Wall Area E) × 100 = (277 ÷ 2,651) × 100
WWR | South WWR Actual (%) | Envelope Summary | Window Opening Area S ÷ Gross Wall Area S | Calculated | 5.06% | 5.06% | (Window Area S ÷ Wall Area S) × 100 = (171 ÷ 3,382) × 100
WWR | West WWR Actual (%) | Envelope Summary | Window Opening Area W ÷ Gross Wall Area W | Calculated | 5.21% | 5.21% | (Window Area W ÷ Wall Area W) × 100 = (155 ÷ 2,975) × 100
WWR | Shading Type / Ratio | Envelope Summary | No shading surfaces in model | Direct read (None/0) | None / 0 | None / 0
Envelope Thermal | Wall U-Value (Btu/h·ft²·°F) | Envelope Summary — Opaque Ext Construction | Casa - Ext Wall Wood Framed / 90.1-10 Min Wall Steel Framed Zone 3 | Direct read | 0.046 | 0.084
Envelope Thermal | Roof U-Value (Btu/h·ft²·°F) | Envelope Summary — Opaque Ext Construction | Casa - Roof Single Ply Tapered / 90.1-10 Min Roof Zone 3 | Direct read | 0.026 | 0.047
Envelope Thermal | Exposed Floor U-Value | Envelope Summary — Floor Construction | 90.1-13 Min Floors Steel Joist Zone 5 / 90.1-10 Min Floors Zone 3 | Direct read | 0.038 | 0.053
Envelope Thermal | Slab on Grade U-Value | Envelope Summary — Slab Construction | Casa - Slab On Grade / 90.1-10 Min Slab Unheated Zone 1-5 | Direct read | 0.041 | 0.041
Envelope Thermal | Glass U-Value | Envelope Summary — Fenestration | 90.1-13 Window Zone 4-6 Metal Oper / 90.1-10 Window Zone 3AB Nonmetal | Direct read | 0.501 | 0.651
Envelope Thermal | Glass SHGC | Envelope Summary — Fenestration | Same constructions as Glass U-Value | Direct read | 0.401 | 0.252
Envelope Thermal | Glass VLT | Envelope Summary — Fenestration | Same constructions as Glass U-Value | Direct read | 0.442 | 0.319
Envelope Thermal | Glass LSG | Derived | VLT ÷ SHGC | Calculated | 1.102 | 1.266 | Light-to-Solar Gain = VLT ÷ SHGC → Proposed: 0.442 ÷ 0.401 ¦ Baseline: 0.319 ÷ 0.252
Envelope Thermal | Wall 2 U-Value | N/A — Single wall construction | Only one wall assembly type in model | N/A | N/A | N/A | Only one exterior wall construction type exists in this project
Envelope Thermal | Vertical Weighted U-Value | Derived | Area-weighted average of opaque wall + glazing | Calculated | 0.0781 | 0.124 | (Opaque Wall Area × Wall U-Value + Window Area × Glass U-Value) ÷ Total Gross Wall Area
Envelope Thermal | Vertical Weighted R-Value | Derived | Inverse of Vertical Weighted U-Value | Calculated | 12.8 | 8.06 | 1 ÷ Vertical Weighted U-Value
Envelope Thermal | Assembly U-Value | Derived | Area-weighted average of opaque wall + roof | Calculated | 0.0342 | 0.0622 | (Opaque Wall Area × Wall U + Roof Area × Roof U) ÷ (Opaque Wall Area + Roof Area)
Envelope Thermal | Infiltration Rate (CFM/ft² facade) | Room Info Entered Values (Baseline & Primary) | Infiltration ACH by room type template | Calculated | 0.0308 | 0.0308 | CFM = ACH × (Room Area × 9 ft ceiling) ÷ 60; summed all rooms; ÷ Gross Facade Area (11,729 ft²) Room type ACH: Occupied=0.13, Corridor=0.07, MEP/Unconditioned=0.0
Lighting / Occ / Equipment | Lighting Power Density (W/ft²) | LEED Summary | Section 1.4 — Building total LPD | Direct read | 0.45 | 0.54
Lighting / Occ / Equipment | Occupant Density (ft²/person) | LEED Summary | Total area ÷ occupant count | Calculated | 168.8 | 168.8 | Total Conditioned Area (ft²) ÷ Total Occupants (125 persons from building program)
Lighting / Occ / Equipment | Equipment Power Density (W/ft²) | LEED Summary | Section 1.4 — Receptacle Equipment Total Power ÷ area | Calculated | 0.69 | 0.69 | Total Receptacle Equipment Power (W) ÷ Conditioned Floor Area (ft²)
Airflow | Total Ventilation CFM | System Component Summary | DOAS airflow (Proposed) / Zone vent sum (Baseline) | Direct read | 1,550 | 1,672
Airflow | Ventilation CFM/ft² | Derived | Total Vent CFM ÷ Conditioned Floor Area | Calculated | 0.1135 | 0.1224 | Total Ventilation CFM ÷ Conditioned Floor Area (13,652 ft²)
Airflow | Total Heating CFM | System Component Summary | Sum of all zone heating supply airflows | Direct read | 4,082 | 10,601
Airflow | Heating CFM/ft² | Derived | Total Heating CFM ÷ Conditioned Floor Area | Calculated | 0.2991 | 0.7765 | Total Heating CFM ÷ Conditioned Floor Area (13,652 ft²)
Airflow | Total Cooling CFM | System Component Summary | Sum of all zone cooling supply airflows | Direct read | 8,767 | 10,601
Airflow | Cooling CFM/ft² | Derived | Total Cooling CFM ÷ Conditioned Floor Area | Calculated | 0.6422 | 0.7765 | Total Cooling CFM ÷ Conditioned Floor Area (13,652 ft²)
System Efficiencies | Chiller COP | N/A | No chilled water plant in either model | N/A | N/A | N/A
System Efficiencies | Boiler COP | N/A | No boiler in either model | N/A | N/A | N/A
System Efficiencies | DX Cooling COP | ASHRAE 90.1-2010 Table 6.8.1B | Baseline PTHP only; Proposed uses VRF (separate field) | Calculated | N/A | 3.19 | Baseline: EER 10.9 (Table 6.8.1B, Zone 3B, PTHP ≤65°F) ÷ 3.412 = COP 3.19
System Efficiencies | DX Heating HSPF | N/A | Baseline captured in HP COP field; Proposed is VRF | N/A | N/A | N/A
System Efficiencies | HP / VRF Cooling COP | ASHRAE 90.1-2010 Table 6.8.1D (Proposed) / 6.8.1B (Baseline) | Zone 3B minimum — VRF (Proposed) / PTHP (Baseline) | Standard reference | 3.2 | 3.19 | Proposed VRF: Table 6.8.1D Zone 3B min COP = 3.2 ¦ Baseline PTHP: EER 10.9 ÷ 3.412 = 3.19
System Efficiencies | HP / VRF Heating COP | ASHRAE 90.1-2010 Table 6.8.1D (Proposed) / 6.8.1B (Baseline) | Zone 3B minimum | Standard reference | 3.3 | 3.2 | Proposed VRF: Table 6.8.1D Zone 3B min heating COP = 3.3 ¦ Baseline PTHP: Table 6.8.1B = 3.2
System Efficiencies | Total Fan Power — Proposed (kW) | System Component Summary Primary | Sum of all supply fan kW | Calculated | 2.73 kW | — | DOAS SF-1 (0.63 kW) + Kitchen CV SF-1 (1.03 kW) + VRF zone fans sum (1.07 kW) = 2.73 kW
System Efficiencies | Total Fan Power — Baseline (kW) | LEED Summary — PRM Fan Power | Sum of PRM allowed fan kW by system | Calculated | — | 6.88 kW | Sys10 (0.02) + Sys2 (0.96) + Sys4 (3.71) + Sys4Copy Kitchen (2.19) = 6.88 kW
System Efficiencies | SHW Thermal Efficiency | System Component Summary Primary | DOAS SCC-1 Desuperheater | ⚠ Flagged | Desuperheater (heat recovery) | N/A | DOAS uses heat recovery desuperheater — no discrete COP exported by TRACE 3D Plus
System Efficiencies | Exterior Lighting (kW) | All reports | No exterior lighting in model | Direct read (0) | 0 | 0

## Legend
Color | Category
Dark Blue Header | Column headers
Light Blue | Project Info
Light Green | Energy Consumption
Yellow | Economics & Carbon
Peach | Peak Loads
Sky Blue | Building Geometry
Mint Green | WWR
Light Red | Envelope Thermal
Pink | Lighting / Occ / Equipment
Green | Airflow
Cornflower Blue | System Efficiencies
Orange (⚠) | Manual entry required or flagged field